## IDIS P2-OBJ 2.0
IDIS Interoperability Specification
Package 2
Smart Metering Objects
Edition 2.0 (including G3-PLC), 03-09-2014
V2.28
Copyright
The content on this document is protected by intellectual property rights (in particular copyright). Third-party content is marked as such. The content must not be copied, disseminated, amended, made accessible to third parties nor used in any other way without explicit written consent of the IDIS Industry Association, except where such use is explicitly permitted by the applicable law.
The use of the idis logo and the idis test label
The IDIS logo is a registered trademark. The use of the logo is regulated by the IDIS Industry Association.
The IDIS test label is granted by the IDIS Industry Association for registered equipment which has passed the IDIS interoperability test. The interoperability testing and the use of the test label is regulated by the IDIS Industry Association.

## Changelog
Date | Version | User | Changes | Remarks
2011-06-10 | 2.00 | DremeljI | Initial object model for IP Profile | The IDIS Package 1 OM modified in the following way: - two new types added - supported object definition done for the two new types (no support for S-FSK objects, support for IP Profile objects)
|  |  | Suppressed the 'Suported attributed/methods' column | All attributes and methods as listed of mandatory and declared optional objects from OM must be visible in the Current association.object_list access_rights part. The access rights must correspond to the access rights defined wiht this OM
|  |  | New type definitions added | send_method_type=struct(enum, octet_string, enum) window_element=struct(octet_string, octet_string) allowed_callers_and_actions_element=struct(octet_string, script9)
callback_data=struct(boolean, unsigned, octet_string) LCP_options_element=struct(unsigned, unsigned, choice(unsigned, boolean, long_unsigned, double_long_unsigned, callback_data))
PPP_authentication_type=choice(null, struct(octet_string, octet_string), struct(octet_string, unsigned), struct(boolean, boolean)) IPCP_options_elemen=struct(unsigned, unsigned, choice(boolean, long_unsigned, double_long_unsigned, array(double_long_unsigned)))
2011-09-15 | 2.01 | DremeljI | Change of Current association.change_HLS_secret access rights to optional Action. | The behaviour and related tests moved to Package 2
|  |  | Change of meter type as agreed at IDIS Assoc meeting in Sencur, 2011-09-15 | Meter type corresponds to Package and 1ph/3ph meter object model. Commuincation designation is no longer part of meter type i.e. 102 can be Pack 2.0 1ph PLC or IP meter
2011-10-14 | 2.02 | DremeljI | Corrections according to the DLMS_021_Push_setup_V1 6 contribution:
-LN for push setup objects
-push setup object attribute names and types
-auto answer changes
-new instance - message handler
-LN for alarm descriptor
2011-10-14 | 2.03 | DremeljI | Corrected IC of the push setup to be according tto the DLMS_021_Push_setup_V1 6 contribution
2011-12-07 | 2.04 | DremeljI | Correction on the maximum length of MBUS profile buffer attribute type
2nd alarm instance added (register, filter, descriptor, monitor)
Auto connect added for controlling different IP modes (always on, on on wake up,…)
NTP setup instance added
GPRS, Ethernet and SMS now marked as optional to allow the choice of the channel through IPv4.DL_reference. The channel chosen in the IPv4.DL reference shall be considered as mandatory i.e. has to be present in the object model
Added IPv6
IPv4 and IPv6 now marked as optional to allow the choice of the IP version through TCP-UDP.IP_reference. The IP version chosen in theTCP-UDP.IP_reference shall be considered as mandatory i.e. has to be present in the object model
Removed the Push setup On Power up since the usecase handled via Push setup On Alarm
Push setup On Power down by default handled via SMS
2011-12-22 |  | DremeljI | New events added, etc...aligned with 111222 IDIS Pack2 IP Profile ed1.0 w1.4
2012-02-28 | 2.05 | DremeljI | Review 1.0 corrections:
Data Notification service is BASIC service and is supported in all Pack 2 configurations Separation between BASIC and extension P is done on object level i.e. Without extension P: registration, alarming, With extension P: rest of use cases
New objects added for Customer Information Push support
Based on object_defs_v2.5 I have put the NTP to IC47, LN0-0:25.6.0.255 and aligned the OM to choice of “no security” or “shared secrets”
Added Alarm register definitions into dedicated tab "Alarms"
Added "Permanent Error on MBUS" events
Removed SMS message handler since the functionality of incoming wakeup SMS controlled by Auto Answer
2012-03-08 | 2.06 | DremeljI | NTP LN and IC updated according to last contribution to dlms UA [DLMS_021_Push_setup_V1.7_CR120308.docx]
Updated auto connect mode according to the last dlms UA contribution [DLMS_021_Push_setup_V1.7_CR120308.docx]
2012-04-12 | 2.07 | DremeljI | Changes according to IDIS Pack 2 profile w2.5
Added 8 new events for MBUS local dis/reconnection
Changed "Customer" to "Consumer" information
Changed the NTP setup.authentication_method default value to only 1 i.e. remove the choice(0,1)
Removed attribute 7 of auto answer
2012-04-13 | 2.08 | DremeljI | Removed column C and D (meter type 104 and 105 since not in scope of Pack 2 Ed1.0)
2012-04-19 |  |  | Auto answer clas version changed
2012-07-02 | 2.09 | DremeljI | Updated according Packacge 2 Ed 1.0 W2.5f modifications
2102-07-26 |  | DremeljI | Updated according Packacge 2 Ed 1.0 W2.6 modifications
2012-08-23 | 2.10 | DremeljI | Removed Auto connect script table since not used
Event 59 now mandatory
2012-11-14 |  | AymonC | New type definitions added | register_assignment_item=struct(long_unsigned,octet_string[6]) execution_time_date=struct(octet_string,octet_string) reply_status=struct(unsigned,unsigned)
Class 6, added the type ''register_assignment_item'' as array element type for attribute 2
Class 7, added the type ''capture_object_definition as array element type for attribute 3
Class 40 (push setup) fixed the default value of attribute send_destination_and_method (struct)
Class 22, added the type execution_time_date as array element type for attribute 4
Class 55, added reply_status as array element type for attribute 3
Class 56, added octet_string as array element type for attribute 2
|  | DremeljI | Removed "P" Extension - M-P -> M and O-P -> O
All remote communication setup objects now marked as optional; each manufacturer shall declare the objects based on the remote communication technology used - GPRS or Ethernet or even GPRS+Ethernet
2012-12-05 |  | DremeljI | corrected predifined type callers_and_actions_element; now called list_of_allowed_callers_element
2013-06-12 | 2.11 | MedjeraN | the default values for executed_script attribute in Push action scheduler - Interval 1-3 object are corrected.
2013-07-02 | 2.12 | MedjeraN | the table of predfined types are extended with execution_time_date and reply_status type
in Predefined types table the comments are designated by uppercase 'C' character
2013-07-17 | 2.13 | AymonC | Extended options for mandatory objects added | see sheet Syntax for value definition
2013-09-24 |  | RahmC | Various changes after review/Telco of 1.7.2013, extensions enhanced (CIP added)
2013-09-25 |  | RahmC | Events updated, Remote Communication Log added, ntp data types aligned with BB proposal
2013-09-26 |  | RahmC | Optional set added to the 'type' attribute of all push schedulers to be in line with all other schedulers
2013-10-02 |  | RahmC | PPP setup is mandatory in case of GPRS only, auto connect is mandatory in all cases, GPRS modem setup, modem configuration, auto answer are not optional anymore but mandatory in case of GPRS.
2013-10-07 |  | RahmC | Add choices for resolution of instantaneous values, reorder and fix entries in push script table, optional set added for attribute executed_script of image activation scheduler, APN size at least 64 bytes, script identifier of customer information push set to 6 | actions following review telco of 7.10.2013
2013-10-28 |  | RahmC | Event numbers adapted to IDIS spec: 159-166 incremented by 1, 159 now reserved
2013-10-31 |  | RahmC | Media specific objects of single phase meters aligned to 3 ph meter
2013-11-11 |  | RahmC | Default values of push setup attributes (number_of _retries and repetition_delay) removed | actions following FIT at the beginning of November 2013
2013-11-15 |  | RahmC | Disconnector script table modified to distnguish between local and remote connection and disconnection
2014-01-16 | 2.14 | RahmC | Removed entry 3 from disconnector script table again M-Bus disconnector, Load mgmt and tariffication script tables updated to align the local and remote connection/disconnection behaviour to the disconnector No access anymore to execution method of load mgmt and disconnector script tables (E and G) Letter 'C' for comments added again in 'Predefined Types' Sheet | actions following Telco of 15.1.2014 and IDIS meeting beginning of January in Zug
2014-01-24 |  | RahmC | IPv6 setup aligned to BB11, additional type added to predefined types section
2014-02-11 |  | MedjeraN | Attribute 2 executed_script of Push Action Scheduler - Cosumer Information is corrected. In previous version attribute was referencing the script 6 in script table 0-0:10.108.255 instead script 8. The values time_date definitions in the attribute execution_time are changed from integers in hexdecimal notation in octet-strings. Structure of IPv6 class and attribute types are aligned with definition in Blue Book 11. The new predefined type IPv6_address_entry is added
2014-02-18 |  | AymonC | Disconnect control scheduler 0-0:15.0.1.255, attribute executed_script, changed from {0-0:10.0.106.255, [1..2]} to {0-0:10.0.106.255, [1..4]}
Push setup - Interval_1 0-1:25.9.0.255, attribute send_destination_and_method, changed from {0, *, 0} to {choice(0,4), *, 0}
2014-05-07 |  | RahmC | Naming of firmware version objects adapted to BB11 Default value of PPP.LCP_options and PPP.IPCP_options extended to allow more than one entry IPv6: neighbour_discovery_setup_element added again to predefined types access rights completed again for attribute 9 and 10
2014-08-22 | 2.20 | RahmC | new option -G3 introduced for the G3 communication stack in the syntax sheet new objects added to support G3 including defualt values and access rights | initial version, based on BB12 contribution 037 "final version 01.08.14"
|  |  | Ethernet Setup renamed to MAC Address Setup and added as mandatory for G3 (and Ethernet) | to be inline with BB
2015-05-07 | 2.21 | AymonC | Option syntax changed, ''¦'' operator allowed | Example M-E¦M-G3
double-long-unsigned replaced by double_long_unsigned
long-unsigned replaced by long_unsigned
bit-string prelaced by bit_string
Replaced FALSE by 0
2015-08-14 | 2.22 | SchaubT | NTP setup, method 3 "delete_authentication_key": double-long replaced by double-long-insigned | to be inline with latest BB proposal
2015-08-25 |  | RahmC | Push script table now has dynamic length (array[6..*])
2015-02-26 | 2.23 | RahmC/MedjeralN | Choices added to cover issues detected during iCTT development
2015-03-08 | 2.24 | MedjeralN | Choice for Push scriptable update with optional cases
2016-05-18 | 2.25 | RahmC | optional SET for attribute "image_block-size" of object "Image transfer"
2016-08-25 | 2.26 | SchaubT | All event objects choice(enum, long_unsigned)
2017-01-24 | 2.27 | RahmC | Data types of M-Bus value registers extended to also cover signed values as per EN13757
2017-04-27 | 2.28 | RahmC/MedjeralN | Optional action request added to add/remove_IPv6_address methods of IPv6 setup object Editorial correction.

## Syntax
Syntax
Syntax of ‘’Attribute Type’’ and ‘’Default Value’’ columns of Object Model file
The { } construction denotes an iteration of 0..n elements
The ¦ construction denotes a variant
The [ ] construction denotes an optional element
V2.28
Syntax for the ‘’Attribute Type’’ column
TypeSpecifier ::= StandardType ¦ PredefinedType
StandardType ::= SimpleType ¦ ArrayType ¦ StructType ¦ OctetStringType ¦ ChoiceType
PredefinedType ::= types defined by the application, for example ass_list_type, and that can be defined with standard types or other predefined types.
SimpleType ::= null ¦ boolean ¦ bit_string ¦ double_long ¦ double_long_unsigned ¦ bcd ¦ integer ¦ long ¦ unsigned ¦ long_unsigned ¦ long64 ¦ long64_unsigned ¦ enum ¦ float32 ¦ float64 ¦ date_time ¦ time ¦ date
ArrayType ::= array [SizeConstraint] [(TypeSpecifier)]
StructType ::= struct{TypeSpecifier {, TypeSpecifier }}
OctetStringType ::= octet_string [SizeConstraint]
ChoiceType ::= choice(TypeSpecifier {, TypeSpecifier})
SizeConstraint ::= [Boundary [..Boundary]]
Boundary ::= IntegerValue ¦ *
Syntax for the Default Value column
Value ::= IntegerValue ¦ RangeValue ¦ StructuredValue ¦ StringValue ¦ VariantValue¦ OBISValue ¦ *
IntegerValue ::= [-] ?sequence of digits? ¦ 0x ?Sequence of hex-digits?
RangeValue ::= [Boundary.. Boundary]
Boundary ::= IntegerValue ¦ *
StructuredValue ::= {Value {, Value} [,…]}
StringValue ::= “\?Sequence of characters? ¦ ?even sequence of hex-digits”
VariantValue ::= choice(Value {,Value})
OBISValue ::= OBISField - OBISField: OBISField. OBISField. OBISField. OBISField
OBISField ::= IntegerValue ¦ RangeValue ¦ *
Extensions which control the supported objects
O=always optional
M=always mandatory
M-x mandatory for extension x
The '-x' defines the condition which applies to M, i.e. mandatory in case the condition is true.
-D=Extension D
-M=Extension M
-L=Extension L
-G=GPRS communication channel is used
-E=Ethernet communication channel is used
-G3=G3 PLC communication channel is used
-I4=IPv4 protocol is used
-I6=IPv6 protocol is used
-C=CIP supported
NA=not applicable
Colour Codes
Group Assignment
Instance
Attribute
Method

## Predefined Types
C | Predefined types
C | type_name=type_string
C | The identifier before the '=' is replaced by the string after the '='
C | No spaces are allowed before and after the '='
C | Types for OM Package 1
asslist_type=array(struct(long_unsigned, octet_string))
object_list_type=array(object_list_element)
object_list_element=struct(long_unsigned, unsigned, octet_string, access_right)
access_right=struct(attribute_access_descriptor, method_access_descriptor)
attribute_access_descriptor=array(attribute_access_item)
method_access_descriptor=array(method_access_item)
attribute_access_item=struct(integer, enum, access_selector)
access_selector=choice(array(integer),null)
method_access_item=struct(integer, enum)
associated_partners_type=struct(integer,long_unsigned)
application_context_name=choice(struct(unsigned, unsigned, long_unsigned, unsigned, unsigned, unsigned, unsigned), octet_string)
xDLMS_context_type=struct(bit_string, long_unsigned, long_unsigned, unsigned, integer, octet_string)
mechanism_name_structure=application_context_name
scal_unit_type=struct(integer, enum)
scripts=array(script9)
script9=struct(long_unsigned, array(action_specification))
action_specification=struct(enum, long_unsigned, octet_string[6], integer, any)
script22=struct(octet_string[6], long_unsigned)
value_definition=struct(long_unsigned, octet_string, integer)
threshold=any
emergency_profile_type=struct(long_unsigned, octet_string, double_long_unsigned)
action_set=struct(action_item, action_item)
action_item=struct(octet_string, long_unsigned)
frequencies_type=struct(double_long_unsigned, double_long_unsigned)
initiator_descriptor=struct(octet_string, long_unsigned, unsigned)
desynchronization_listing_type=struct(double_long_unsigned, double_long_unsigned, double_long_unsigned, double_long_unsigned, double_long_unsigned)
capture_object_definition=struct(long_unsigned, octet_string, integer, long_unsigned)
C | Additional types for OM Package 2
send_destination_and_method_type=struct(enum, octet_string, enum)
window_element=struct(octet_string, octet_string)
caller_id=(octet_string)
list_of_allowed_callers_element=struct(octet_string, enum)
sender_id=(octet_string)
senders_and_actions_element=struct(octet_string, script22)
callback_data=struct(boolean, unsigned, octet_string)
LCP_options_element=struct(unsigned, unsigned, choice(unsigned, boolean, long_unsigned, double_long_unsigned, callback_data))
IPCP_options_element=struct(unsigned, unsigned, choice(boolean, long_unsigned, double_long_unsigned, array(double_long_unsigned)))
PPP_authentication_type=choice(NULL, struct(octet_string, octet_string), struct(octet_string, unsigned), struct(boolean, boolean, boolean))
quality_of_service_type=struct(qos_element, qos_element)
qos_element=struct(unsigned, unsigned, unsigned, unsigned, unsigned)
nr_rings_type=struct(unsigned, unsigned)
IPv6_address=octet_string[0..48]
IPv6_address_entry=(enum, IPv6_address)
register_assignment_item=struct(long_unsigned,octet_string[6])
execution_time_date=struct(octet_string,octet_string)
reply_status=struct(unsigned,unsigned)
neighbour_discovery_setup_element=struct(unsigned,long_unsigned,double_long_unsigned)

## Object model
# | Object / Attribute Name | Supported Objects |  | Attribute Type | IC |  | SN | OBIS code / Default Value | Access rights [Get, Set, Action], optional if in '( )' |  |  | Comments
| Object / Attribute Name | 102 1ph IP | 103 3ph IP | Attribute Type | Class | Ver. |  | OBIS code / Default Value | Public (16) | Preestablished (102) | Management (1)
Abstract objects - Association & Security
| SAP Assignment | M | M |  | 17 | 0 | 0xFC00 | 0-0:41.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000290000FF" | Get | -- | Get
2 | SAP_assignment_list |  |  | asslist_type |  |  | 0x08 | {{1, *}} | Get | -- | Get | One logical device, Server SAP 1
1 | connect_logical_device | [5 empty] | 0x20 |  | -- | -- | --
| Current association | M | M |  | 15 | 1 |  | 0-0:40.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000280000FF" | Get | -- | Get
2 | object_list |  |  | object_list_type |  |  | 0x08 |  | Get | -- | Get
3 | associated_partners_id |  |  | associated_partners_type |  |  | 0x10 |  | Get | -- | Get
4 | application_context_name |  |  | application_context_name |  |  | 0x18 |  | Get | -- | Get
5 | xDLMS_context_info |  |  | xDLMS_context_type |  |  | 0x20 |  | Get | -- | Get
6 | authentication_mechanism_name |  |  | mechanism_name_structure |  |  | 0x28 |  | Get | -- | Get, (Set) | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret |  |  | octet_string |  |  | 0x30 |  | -- | -- | (Set) | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status |  |  | enum |  |  | 0x38 |  | Get | -- | Get
9 | security_setup_reference |  |  | octet_string[6] |  |  | 0x40 | "00002B0000FF" | Get | -- | Get
1 | reply_to_HLS_authentication | [5 empty] | 0x60 |  | -- | -- | Action
2 | change_HLS_secret | [5 empty] | 0x68 |  | -- | -- | (Action) | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object | [5 empty] | 0x70 |  | -- | -- | --
4 | remove_object | [5 empty] | 0x78 |  | -- | -- | --
| Security setup | M | M |  | 64 | 0 |  | 0-0:43.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00002B0000FF" | -- | -- | Get
2 | security_policy |  |  | enum |  |  | 0x08 |  | -- | -- | Get,Set
3 | security_suite |  |  | enum |  |  | 0x10 | 0 | -- | -- | Get,Set | 0 = AES-GCM-128/AES-128
4 | client_system_title |  |  | octet_string[8] |  |  | 0x18 |  | -- | -- | Get
5 | server_system_title |  |  | octet_string[8] |  |  | 0x20 |  | -- | -- | Get
1 | security_activate |  |  | enum |  |  | 0x28 |  | -- | -- | Action
2 | global_key_transfer |  |  | key_data |  |  | 0x30 |  | -- | -- | Action
| Security - Receive frame counter - broadcast key | M | M |  | 1 | 0 |  | 0-0:43.1.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00002B0101FF" | Get | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | Get | -- | Get
| Security - Receive frame counter - unicast key | M | M |  | 1 | 0 |  | 0-0:43.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00002B0100FF" | Get | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | Get | -- | Get
Abstract objects - ID's & Control information
| COSEM logical device name | M | M |  | 1 | 0 | 0xFD00 | 0-0:42.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00002A0000FF" | Get | -- | Get
2 | value |  |  | octet_string[16] |  |  | 0x08 |  | Get | -- | Get | unique identification of the logical device
| Device ID 1, manufacturing number | M | M |  | 1 | 0 |  | 0-0:96.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600100FF" | -- | -- | Get
2 | value |  |  | octet_string[0..16] |  |  | 0x08 |  | -- | -- | Get | E-meter serial number (Serial number of the device, handled by the manufacturer); ASCII coded
| Device ID 2 | M | M |  | 1 | 0 |  | 0-0:96.1.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600101FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get,Set | E-meter equipment identifier
| Device ID 3 | M | M |  | 1 | 0 |  | 0-0:96.1.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600102FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get,Set | function location
| Device ID 4 | M | M |  | 1 | 0 |  | 0-0:96.1.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600103FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get,Set | location information
| Device ID 5 | M | M |  | 1 | 0 |  | 0-0:96.1.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600104FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get,Set | no special meaning defined
| Device ID 6, IDIS certification number | M | M |  | 1 | 0 |  | 0-0:96.1.5.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600105FF" | -- | -- | Get
2 | value |  |  | octet_string[0..16] |  |  | 0x08 |  | -- | -- | Get | IDIS certification number
| Currently active energy tariff | M | M |  | 1 | 0 |  | 0-0:96.14.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600E00FF" | -- | -- | Get
2 | value |  |  | octet_string[0..8] |  |  | 0x08 |  | -- | -- | Get | currently active tariff = active_mask of register activation object (mask_name of the 0-0:14.0.1.255) Empty octet string represents no tariff is active.
Abstract objects - Time related issues
| Clock | M | M |  | 8 | 0 |  | 0-0:1.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000010000FF" |  |  | Get
2 | time |  |  | octet_string[12] |  |  | 0x08 |  | -- | Set | Get, Set | Current date and time as local time, deviation can be handeled or set to 0x8000, status must be handled. With Set deviation=0x8000 and status=0xFF
3 | time_zone |  |  | long |  |  | 0x10 | -60 | -- | Set | Get, Set
4 | status |  |  | unsigned |  |  | 0x18 |  | -- |  | Get
5 | daylights_savings_begin |  |  | octet_string[12] |  |  | 0x20 | "FFFF03FE07020000008000FF" | -- | Set | Get, Set | last sunday in March at 02:00
6 | daylights_savings_end |  |  | octet_string[12] |  |  | 0x28 | "FFFF0AFE07030000008000FF" | -- | Set | Get, Set | last sunday in October at 03:00
7 | daylights_savings_deviation |  |  | integer |  |  | 0x30 | 60 | -- | Set | Get, Set
8 | daylights_savings_enabled |  |  | boolean |  |  | 0x38 | 1 | -- | Set | Get, Set
9 | clock_base |  |  | enum |  |  | 0x40 | 1 | -- |  | Get | internal crystal (by default)
| Local Time | O | O |  | 1 | 0 |  | 1-0:0.9.1.255 |  |  |  | For display and readout purposes, not used for remote communication
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100000901FF" | -- | -- | Get
2 | value |  |  | octet_string[4] |  |  | 0x08 |  | -- | -- | Get
| Local Date | O | O |  | 1 | 0 |  | 1-0:0.9.2.255 |  |  |  | For display and readout purposes, not used for remote communication
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100000902FF" | -- | -- | Get
2 | value |  |  | octet_string[5] |  |  | 0x08 |  | -- | -- | Get
| Clock Time Shift Limit | M | M |  | 3 | 0 |  | 1-0:0.9.11.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "010000090BFF" | -- | -- | Get
2 | value |  |  | unsigned |  |  | 0x08 | 60 | -- | Set | Get, Set | Maximum allowed time shift without registration of a time shift event
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | --
| NTP setup | O | O |  | 100 | 0 |  | 0-0:25.10.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000190A00FF" | -- | -- | Get
2 | activated |  |  | boolean |  |  | 0x08 | 0 | -- | Set | Get, Set
3 | server_address |  |  | octet_string[0..*] |  |  | 0x10 |  | -- | -- | Get, Set
4 | server_port |  |  | long_unsigned |  |  | 0x18 |  | -- | -- | Get, Set
5 | authentication_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get, Set | Only "no secret" or "shared secrets" supported.
6 | authentication_keys |  |  | array |  |  | 0x28 |  | -- | -- | Set
7 | client_key |  |  | octet_string[0..*] |  |  | 0x30 |  | -- | -- | Set
1 | synchronize_time |  |  | integer |  |  | 0x38 |  | -- | Action | Action
2 | add_authentication_key |  |  | structure |  |  | 0x40 |  | -- | -- | --
3 | delete _authentication_key |  |  | double_long_unsigned |  |  | 0x48 |  | -- | -- | --
| Activity Calendar | M | M |  | 20 | 0 |  | 0-0:13.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000D0000FF" | -- | -- | Get
2 | calendar_name_active |  |  | octet_string[0..8] |  |  | 0x08 |  | -- | -- | Get | The calendar_name_active has a size of 8 characters at least, i.e. [0..8] is mandatory but can be longer
3 | season_profile_active |  |  | array[0..*] |  |  | 0x10 |  | -- | -- | Get
4 | week_profile_table_active |  |  | array[0..*] |  |  | 0x18 |  | -- | -- | Get
5 | day_profile_table_active |  |  | array[0..*] |  |  | 0x20 |  | -- | -- | Get
6 | calendar_name_passive |  |  | octet_string[0..8] |  |  | 0x28 |  | -- | Set | Get, Set | see calendar_name_active
7 | season_profile_passive |  |  | array[0..*] |  |  | 0x30 |  | -- | Set | Get, Set
8 | week_profile_table_passive |  |  | array[0..*] |  |  | 0x38 |  | -- | Set | Get, Set
9 | day_profile_table_passive |  |  | array[0..*] |  |  | 0x40 |  | -- | Set | Get, Set
10 | activate_passive_calendar_time |  |  | octet_string[12] |  |  | 0x48 |  | -- | Set | Get, Set
1 | activate_passive_calendar |  |  | integer |  |  | 0x50 |  | -- | (Action) | (Action)
| Special Days Table | M | M |  | 11 | 0 |  | 0-0:11.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000B0000FF" | -- | -- | Get
2 | entries |  |  | array[0..30] |  |  | 0x08 |  | -- | Set | Get, Set
| Register activation - Energy | M | M |  | 6 | 0 |  | 0-0:14.0.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000E0001FF" | -- | -- | Get
2 | register_assignment |  |  | array[32..*](register_assignment_item) |  |  | 0x08 |  | -- | (Set) | Get, (Set) | Array size depends on the amount of rated registers supported; 32 mandatory, others optional
3 | mask_list |  |  | array[0..*] |  |  | 0x10 |  | -- | Set | Get, Set
4 | active_mask |  |  | octet_string[0..8] |  |  | 0x18 |  | -- | -- | Get
| Register activation - Maximum Demand | M | M |  | 6 | 0 |  | 0-0:14.0.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000E0002FF" | -- | -- | Get
2 | register_assignment |  |  | array[16..*](register_assignment_item) |  |  | 0x08 |  | -- | (Set) | Get, (Set) | Array size depends on the amount of rated registers supported; 16 mandatory, others optional
3 | mask_list |  |  | array[0..*] |  |  | 0x10 |  | -- | Set | Get, Set
4 | active_mask |  |  | octet_string[0..8] |  |  | 0x18 |  | -- | -- | Get
| Tariffication script table | M | M |  | 9 | 0 |  | 0-0:10.0.100.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000A0064FF" | -- | -- | Get
2 | scripts |  |  | scripts |  |  | 0x08 | Choice( // First variant { {1,{ {1,6,0-0:14.0.1.255,4,*}, {1,6,0-0:14.0.2.255,4,*}, {1,70,0-1:96.3.10.255,3,[1..2]} } }, {2,{ {1,6,0-0:14.0.1.255,4,*}, {1,6,0-0:14.0.2.255,4,*}, {1,70,0-1:96.3.10.255,3,[1..2]} } }, {3,{ {1,6,0-0:14.0.1.255,4,*}, {1,6,0-0:14.0.2.255,4,*}, {1,70,0-1:96.3.10.255,3,[1..2]} } }, {4,{ {1,6,0-0:14.0.1.255,4,*}, {1,6,0-0:14.0.2.255,4,*}, {1,70,0-1:96.3.10.255,3,[1..2]} } } ,... }, // Second variant { {1,{ {1,6,0-0:14.0.1.255,4,*}, {1,6,0-0:14.0.2.255,4,*} } }, {2,{ {1,6,0-0:14.0.1.255,4,*}, {1,6,0-0:14.0.2.255,4,*} } }, {3,{ {1,6,0-0:14.0.1.255,4,*}, {1,6,0-0:14.0.2.255,4,*} } }, {4,{ {1,6,0-0:14.0.1.255,4,*}, {1,6,0-0:14.0.2.255,4,*} } } ,... } ) | -- | -- | Get, Set | Set to be able to add also the tariff activation script for load management.
1 | execute |  |  | long_unsigned |  |  | 0x20 |  | -- | -- | (Action) | Execute typically not needed since tariffication always controlled only internaly, never over remote communication.
Abstract objects - Billing period reset
| Predefined Scripts - MDI reset / end of billing period | M | M |  | 9 | 0 |  | 0-0:10.0.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000A0001FF" | -- | -- | Get
2 | scripts |  |  | scripts |  |  | 0x08 |  | -- | -- | (Get) | The attribute's access rights must be declared in CTI file. Allowed possibilities - no access or Get access
1 | execute |  |  | long_unsigned |  |  | 0x20 | 1 | -- | -- | Action | The activation of this scripts is performed by calling the execute() method to the script identifier 1 of the corresponding script object
| End of billing period 1 scheduler | M | M |  | 22 | 0 |  | 0-0:15.0.0.255 |  |  |  | Single action scheduler for Stored Billing Values Profile
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000F0000FF" | -- | -- | Get
2 | executed_script |  |  | script22 |  |  | 0x08 | {0-0:10.0.1.255,1} | -- | -- | Get | "MDI reset / end of billing period"
3 | type |  |  | enum |  |  | 0x10 | 1 | -- | -- | Get, (Set) | 1 is mandatory (Other are optional. If only type 1 is supported Set is optional)
4 | execution_time |  |  | array[0..1](execution_time_date) |  |  | 0x18 |  | -- | -- | Get, Set | at midnight (or any other time) of the first day of every month; the execution can be disabled with writing empty array or {{"FFFFFFFF", "FFFFFFFFFF"}}
| Data of billing period 1 | M | M |  | 7 | 1 |  | 0-0:98.1.0.255 |  |  |  | Stored Billing Values Profile
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000620100FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range and entry
3 | capture_objects |  |  | array[1..*](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {3,1-0:1.8.1.255,2,0}, {3,1-0:1.8.2.255,2,0}, {3,1-0:2.8.1.255,2,0}, {3,1-0:2.8.2.255,2,0}, ...} | -- | -- | Get, Set | clock;+A rate 1;+A rate 2;−A rate 1;−A rate 2; etc.
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [13..*] | -- | -- | Get | ≥ 13 months
1 | reset |  |  | integer |  |  | 0x58 |  | -- | -- | Action
Abstract objects - Disconnector, Load mgmt, Supervision
| Disconnect control scheduler | M-D | M-D |  | 22 | 0 |  | 0-0:15.0.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000F0001FF" | -- | -- | Get
2 | executed_script |  |  | script22 |  |  | 0x08 | {0-0:10.0.106.255, [1..4]} | -- | -- | Get, Set | Connect or disconnect script of disconnector script table (0-0:10.0.106.255)
3 | type |  |  | enum |  |  | 0x10 | 1 | -- | -- | Get, (Set) | 1 is mandatory (others are optional. If only type 1 is supported Set is optional)
4 | execution_time |  |  | array[0..1](execution_time_date) |  |  | 0x18 |  | -- | -- | Get, Set | dedicated timepoint for connection or disconnection; the execution can be disabled with writing empty array or {{"FFFFFFFF", "FFFFFFFFFF"}}
| Disconnector script table | M-D | M-D |  | 9 | 0 |  | 0-0:10.0.106.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000A006AFF" | -- | -- | Get
2 | scripts |  |  | array[4](script9) |  |  | 0x08 | { {1,{{1,70,0-0:96.3.10.255,3,2}}}, //set to ready_for_reconnection {2,{{1,70,0-0:96.3.10.255,3,1}}}, //set to connected {3,{{2,70,0-0:96.3.10.255,1,0}}}, //execute remote disconnect {4,{{2,70,0-0:96.3.10.255,2,0}}}, //execute remote connect } | -- | -- | Get | connect and disconnect scripts, 1 and 2 model local disconnection and local reconnection, 3 and 4 model remote disconnection and connection
1 | execute |  |  | long_unsigned |  |  | 0x20 |  | -- | -- | -- | Executes the script specified in parameter data. If data matches one of the script_identifiers in the script table, then the corresponding action_specification is executed. No direct method call possible via remote communication
| Disconnect control | M-D | M-D |  | 70 | 0 |  | 0-0:96.3.10.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "000060030AFF" | -- | -- | Get
2 | output_state |  |  | boolean |  |  | 0x08 |  | -- | -- | Get
3 | control_state |  |  | enum |  |  | 0x10 |  | -- | -- | Get
4 | control_mode |  |  | enum |  |  | 0x18 |  | -- | -- | Get, Set | if only one conrol mode is available set is not allowed.
1 | remote_disconnect |  |  | integer |  |  | 0x20 |  | -- | -- | Action
2 | remote_connect |  |  | integer |  |  | 0x28 |  | -- | -- | Action
| Event Object - Disconnector Control log | M-D | M-D |  | 1 | 0 |  | 0-0:96.11.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600B02FF" | -- | -- | Get
2 | value |  |  | choice(enum, long_unsigned) |  |  | 0x08 |  | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255; at first power up or if no events were yet generated the value should return 255
| Disconnector Control Log | M-D | M-D |  | 7 | 1 |  | 0-0:99.98.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000636202FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2..3](capture_object_definition) |  |  | 0x10 | {{8, 0-0:1.0.0.255, 2, 0}, {1, 0-0:96.11.2.255, 2, 0}, {71, 0-0:17.0.0.255, 3, 0}} | -- | -- | Get, (Set) | clock;control event code;limiter threshold
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [10..*] | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x58 |  | -- | -- | Action
| Load Mgmt script table | M-L | M-L |  | 9 | 0 |  | 0-0:10.0.103.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000A0067FF" | -- | -- | Get
2 | scripts |  |  | array[4..*](script9) |  |  | 0x08 | { {1,{{1,70,0-1:96.3.10.255,3,2}}}, {2,{{1,70,0-1:96.3.10.255,3,1}}}, {3,{{2,70,0-1:96.3.10.255,1,0}}}, {4,{{2,70,0-1:96.3.10.255,2,0}}}, ... } | -- | -- | Get | connect and disconnect methods of the load mgmt objects (relays), see also disconnector script table for further details
1 | execute |  |  | long_unsigned |  |  | 0x20 |  | -- | -- | -- | Executes the script specified in parameter data. If data matches one of the script_identifiers in the script table, then the corresponding action_specification is executed. No direct method call possible via remote communication
| Load Mgmt - Relay control 1 | M-L | M-L |  | 70 | 0 |  | 0-1:96.3.10.255 |  |  |  | Channel (filed B) to be incremented if additional instances needed
1 | logical_name |  |  | octet_string[6] |  |  |  | "000160030AFF" | -- | -- | Get
2 | output_state |  |  | boolean |  |  | 0x08 |  | -- | -- | Get
3 | control_state |  |  | enum |  |  | 0x10 |  | -- | -- | Get
4 | control_mode |  |  | enum |  |  | 0x18 | 6 | -- | -- | Get, (Set) | If only one control mode is supported then control mode shall be 6. If more than one mode is supported then optional Set should be allowed. For relay only mode 4 or 6 should be used.
1 | remote_disconnect |  |  | integer |  |  | 0x20 |  | -- | -- | Action
2 | remote_connect |  |  | integer |  |  | 0x28 |  | -- | -- | Action
| Load Mgmt - Relay control 2 | O | O |  | 70 | 0 |  | 0-2:96.3.10.255 |  |  |  | Channel (filed B) to be incremented if additional instances needed
1 | logical_name |  |  | octet_string[6] |  |  |  | "000260030AFF" | -- | -- | Get
2 | output_state |  |  | boolean |  |  | 0x08 |  | -- | -- | Get
3 | control_state |  |  | enum |  |  | 0x10 |  | -- | -- | Get
4 | control_mode |  |  | enum |  |  | 0x18 | 6 | -- | -- | Get, (Set) | If only one control mode is supported then control mode shall be 6. If more than one mode is supported then optional Set should be allowed. For relay only mode 4 or 6 should be used.
1 | remote_disconnect |  |  | integer |  |  | 0x20 |  | -- | -- | Action
2 | remote_connect |  |  | integer |  |  | 0x28 |  | -- | -- | Action
| Limiter | M-D | M-D |  | 71 | 0 |  | 0-0:17.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000110000FF" | -- | -- | Get
2 | monitored_value |  |  | value_definition |  |  | 0x08 | choice( {3, 1-0:90.7.0.255, 2}, {5,1-0:1.24.0.255, 2}, {5,1-0:15.24.0.255, 2}) | -- | -- | Get, Set | instantaneous current or sliding demand
3 | threshold_active |  |  | threshold |  |  | 0x10 |  | -- | -- | Get
4 | threshold_normal |  |  | threshold |  |  | 0x18 |  | -- | -- | Get, Set
5 | treshold_emergency |  |  | threshold |  |  | 0x20 |  | -- | -- | Get, Set
6 | min_over_threshold_duration |  |  | double_long_unsigned |  |  | 0x28 | 180 | -- | -- | Get, Set
7 | min_under_threshold_duration |  |  | double_long_unsigned |  |  | 0x30 | 180 | -- | -- | Get, Set
8 | emergency_profile |  |  | emergency_profile_type |  |  | 0x38 |  | -- | -- | Get, Set
9 | emergency_profile_group_id_list |  |  | array |  |  | 0x40 |  | -- | -- | Get, Set
10 | emergency_profile_active |  |  | boolean |  |  | 0x48 |  | -- | -- | Get
11 | actions |  |  | action_set |  |  | 0x50 | choice( { {0-0:10.0.106.255,1} , {0-0:10.0.106.255,2}}, { {0-0:10.0.106.255,1} , {0-0:10.0.106.255,0}} ) | -- | -- | Get, (Set)
| Supervision monitor 1 - Fuse supervision L1 | M-D | M-D |  | 21 | 0 |  | 1-0:31.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01001F0400FF" | -- | -- | Get
2 | thresholds |  |  | array[1] |  |  | 0x08 |  | -- | -- | Get, Set | The threshold is of the same type as the monitored attribute of the referenced object
3 | monitored_value |  |  | value_definition |  |  | 0x10 | {5, 1-0:31.4.0.255, 2} | -- | -- | Get, Set | Instantaneous value current per phase or average current for supervision
4 | actions |  |  | array[1](action_set) |  |  | 0x18 | choice( {{{0-0:10.0.106.255,1} , {0-0:10.0.106.255,2}}}, {{{0-0:10.0.106.255,1} , {0-0:10.0.106.255,0}}} ) | -- | -- | Get, Set
| Supervision monitor 2 - Fuse supervision L2 | NA | M-D |  | 21 | 0 |  | 1-0:51.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100330400FF" | -- | -- | Get
2 | thresholds |  |  | array[1] |  |  | 0x08 |  | -- | -- | Get, Set | The threshold is of the same type as the monitored attribute of the referenced object
3 | monitored_value |  |  | value_definition |  |  | 0x10 | {5, 1-0:51.4.0.255, 2} | -- | -- | Get, Set | Instantaneous value current per phase or average current for supervision
4 | actions |  |  | array[1](action_set) |  |  | 0x18 | choice( {{{0-0:10.0.106.255,1} , {0-0:10.0.106.255,2}}}, {{{0-0:10.0.106.255,1} , {0-0:10.0.106.255,0}}} ) | -- | -- | Get, Set
| Supervision monitor 3 - Fuse supervision L3 | NA | M-D |  | 21 | 0 |  | 1-0:71.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100470400FF" | -- | -- | Get
2 | thresholds |  |  | array[1] |  |  | 0x08 |  | -- | -- | Get, Set | The threshold is of the same type as the monitored attribute of the referenced object
3 | monitored_value |  |  | value_definition |  |  | 0x10 | {5, 1-0:71.4.0.255, 2} | -- | -- | Get, Set | Instantaneous value current per phase or average current for supervision
4 | actions |  |  | array[1](action_set) |  |  | 0x18 | choice( {{{0-0:10.0.106.255,1} , {0-0:10.0.106.255,2}}}, {{{0-0:10.0.106.255,1} , {0-0:10.0.106.255,0}}} ) | -- | -- | Get, Set
Abstract objects - Errors & Alarms, Event logs
| Error Register | M | M |  | 1 | 0 |  | 0-0:97.97.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000616100FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get, Set
| Alarm Register 1 | M | M |  | 1 | 0 |  | 0-0:97.98.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000616200FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get, Set
| Alarm Filter 1 | M | M |  | 1 | 0 |  | 0-0:97.98.10.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "000061620AFF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get, Set | This filter defines, if an event is handled as an alarm when it appears
| Alarm Descriptor 1 | M | M |  | 1 | 0 |  | 0-0:97.98.20.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000616214FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get, Set | Updated on Alarm register change i.e. on 0->1 transition of any of the bits in Alarm register the corresponding bit in the Alarm descriptor is set
| Alarm Monitor 1 | M | M |  | 21 | 0 |  | 0-0:16.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000100100FF" | -- | -- | Get
2 | thresholds |  |  | array[1](double_long_unsigned) |  |  | 0x08 | {0} | -- | -- | Get | Monitored value is Alarm descriptor 1. Value 0 in threshold means if any of the bits in monitor value is newly triggered the action of the monitor will be set.
3 | monitored_value |  |  | value_definition |  |  | 0x10 | {1, 0-0:97.98.20.255, 2} | -- | -- | Get
4 | actions |  |  | array[1](action_set) |  |  | 0x18 | {{{0-0:10.0.108.255,4} , {0-0:10.0.108.255,0}}} | -- | -- | Get, Set | triggers push on alarm in case of occurence, no action is triggered in case the alarm descriptor is cleared
| Alarm Register 2 | M | M |  | 1 | 0 |  | 0-0:97.98.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000616201FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get, Set
| Alarm Filter 2 | M | M |  | 1 | 0 |  | 0-0:97.98.11.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "000061620BFF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get, Set | This filter defines, if an event is handled as an alarm when it appears
| Alarm Descriptor 2 | M | M |  | 1 | 0 |  | 0-0:97.98.21.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000616215FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get, Set | Updated on Alarm register change i.e. on 0->1 transition of any of the bits in Alarm register the corresponding bit in the Alarm descriptor is set
| Alarm Monitor 2 | M | M |  | 21 | 0 |  | 0-0:16.1.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000100101FF" | -- | -- | Get
2 | thresholds |  |  | array[1](double_long_unsigned) |  |  | 0x08 | {0} | -- | -- | Get | Monitored value is Alarm descriptor 2. Value 0 in threshold means if any of the bits in monitor value is newly triggered the action of the monitor will be set.
3 | monitored_value |  |  | value_definition |  |  | 0x10 | {1, 0-0:97.98.21.255, 2} | -- | -- | Get
4 | actions |  |  | array[1](action_set) |  |  | 0x18 | {{{0-0:10.0.108.255,4} , {0-0:10.0.108.255,0}}} | -- | -- | Get, Set | triggers push on alarm in case of occurence, no action is triggered in case the alarm descriptor is cleared
| Event Object - Standard Event Log | M | M |  | 1 | 0 |  | 0-0:96.11.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600B00FF" | -- | -- | Get
2 | value |  |  | choice(enum, long_unsigned) |  |  | 0x08 |  | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| Standard Event Log | M | M |  | 7 | 1 |  | 0-0:99.98.0.255 |  |  |  | Standard event log containing errors and alarms
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000636200FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.0.255,2,0}} | -- | -- | Get, (Set) | clock;event code
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [100..*] | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x58 |  | -- | -- | Action
| Event Object - Fraud Detection Log | M | M |  | 1 | 0 |  | 0-0:96.11.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600B01FF" | -- | -- | Get
2 | value |  |  | choice(enum, long_unsigned) |  |  | 0x08 |  | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| Fraud Detection Log | M | M |  | 7 | 1 |  | 0-0:99.98.1.255 |  |  |  | Event log containing all fraud detection events
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000636201FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.1.255,2,0}} | -- | -- | Get, (Set) | clock;tamper event code
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [30..*] | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x58 |  | -- | -- | Action
| Event Object - Communication Log | M | M |  | 1 | 0 |  | 0-0:96.11.5.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600B05FF" | -- | -- | Get
2 | value |  |  | choice(enum, long_unsigned) |  |  | 0x08 |  | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| Communication Log | M | M |  | 7 | 1 |  | 0-0:99.98.5.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000636205FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.5.255,2,0}} | -- | -- | Get, (Set) | clock;communication event code
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [100..*] | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x58 |  | -- | -- | Action
Abstract objects - User Interface
| Consumer Message Code - Meter Display | M | M |  | 1 | 0 |  | 0-0:96.13.1.255 |  |  |  | Consumer message code shown on meter's display
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600D01FF" | -- | -- | Get
2 | value |  |  | octet_string[0..64] |  |  | 0x08 |  | -- | Set | Get, Set | Message code to be shown on numeric display.
| Consumer Message Text - Consumer Information | M | M |  | 1 | 0 |  | 0-0:96.13.0.255 |  |  |  | Consumer message text sent to End consumer interface
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600D00FF" | -- | -- | Get
2 | value |  |  | octet_string[0..1024] |  |  | 0x08 |  | -- | Set | Get, Set | Message text sent to an external device without any further interpretation
| Push action scheduler - Consumer Information | M-C | M-C |  | 22 | 0 |  | 0-4:15.0.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00040F0004FF" | -- | -- | Get
2 | executed_script |  |  | script22 |  |  | 0x08 | {0-0:10.0.108.255,8} | -- | -- | Get, (Set)
3 | type |  |  | enum |  |  | 0x10 | 5 | -- | -- | Get, (Set)
4 | execution_time |  |  | array[0..*](execution_time_date) |  |  | 0x18 | { {"FFFF0000" , "FFFFFFFFFF"}, {"FFFF0F00" , "FFFFFFFFFF"}, {"FFFF1E00" , "FFFFFFFFFF"}, {"FFFF2D00" , "FFFFFFFFFF"}, } | -- | -- | Get, Set | By default push every 15 seconds
| Push setup - Consumer Information | M-C | M-C |  | 40 | 0 |  | 0-6:25.9.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0006190900FF" | -- | -- | Get
2 | push_object_list |  |  | array[0..*](capture_object_definition) |  |  | 0x08 |  | -- | -- | Get, Set
3 | send_destination_and_method |  |  | send_destination_and_method_type |  |  | 0x10 | {5,"0001160000FF",0} | -- | -- | Get, Set
4 | communication_window |  |  | array[0..*](window_element) |  |  | 0x18 |  | -- | -- | Get, Set
5 | randomisation_start_interval |  |  | long_unsigned |  |  | 0x20 | 0 | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
6 | number_of_retries |  |  | unsigned |  |  | 0x28 |  | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
7 | repetition_delay |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get, Set | Delay in seconds between repetitions
1 | push |  |  | integer |  |  | 0x38 |  | -- | Action | Action
| Security setup - Consumer Information | M-C | M-C |  | 64 | 0 |  | 0-0:43.0.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00002B0001FF" | -- | -- | Get
2 | security_policy |  |  | enum |  |  | 0x08 | 3 | -- | -- | Get,Set
3 | security_suite |  |  | enum |  |  | 0x10 | 0 | -- | -- | Get,Set | 0 = AES-GCM-128/AES-128
4 | client_system_title |  |  | octet_string[8] |  |  | 0x18 |  | -- | -- | Get
5 | server_system_title |  |  | octet_string[8] |  |  | 0x20 |  | -- | -- | Get
1 | security_activate |  |  | enum |  |  | 0x28 |  | -- | -- | Action
2 | global_key_transfer |  |  | key_data |  |  | 0x30 |  | -- | -- | Action
| IEC HDLC setup - Consumer Information Interface | M-C | M-C |  | 23 | 1 |  | 0-1:22.0.0.255 |  |  |  | Mandatory HDLC on Optical port.
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001160000FF" | -- | -- | Get
2 | comm_speed |  |  | enum |  |  | 0x08 |  | -- | Set | Get, Set
3 | window_size_transmit |  |  | unsigned |  |  | 0x10 |  | -- | Set | Get, Set
4 | window_size_receive |  |  | unsigned |  |  | 0x18 |  | -- | Set | Get, Set
5 | max_info_field_lenght_transmit |  |  | long_unsigned |  |  | 0x20 |  | -- | Set | Get, Set
6 | max_info_field_lenght_receive |  |  | long_unsigned |  |  | 0x28 |  | -- | Set | Get, Set
7 | inter_octet_time_out |  |  | long_unsigned |  |  | 0x30 |  | -- | Set | Get, Set
8 | inactivity_time_out |  |  | long_unsigned |  |  | 0x38 |  | -- | Set | Get, Set
9 | device_address |  |  | long_unsigned |  |  | 0x40 |  | -- | -- | Get, Set
Abstract objects - Firmware Upgrade
| Image transfer | M | M |  | 18 | 0 |  | 0-0:44.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00002C0000FF" | -- | -- | Get
2 | image_block_size |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get, (Set) | block size in bytes
3 | image_transferred_block_status |  |  | bit_string |  |  | 0x10 |  | -- | -- | Get | each bit provides info abouot one individual image block 0 = not transferred 1 = transferred
4 | image_first not_transferred_block_number |  |  | double_long_unsigned |  |  | 0x18 |  | -- | -- | Get | provides block number of the first missing block
5 | image_transfer_enabled |  |  | boolean |  |  | 0x20 |  | -- | -- | Get, Set | enabled or not; detail information in image_transfer_status FALSE = disabled TRUE = enabled
6 | image_transfer status |  |  | enum |  |  | 0x28 |  | -- | -- | Get | detailed status of image transfer process 0 = transfer not initiated (not active; default state) 1 = transfer initiated 2 = verification initiated 3 = verification successful 4 = verification failed 5 = activation initiated 6 = activation successful 7 = activation failed
7 | image_to_activate_info |  |  | array |  |  | 0x30 |  | -- | -- | Get
1 | image_transfer_initiate |  |  | structure |  |  | 0x40 |  | -- | -- | Action | initiates the transfer process; includes data in format { image_identifier image_size }
2 | image_block_transfer |  |  | structure |  |  | 0x48 |  | -- | Action | Action | transfers one single block; includes data in format { image_block_number image_block_value }
3 | image_verify |  |  | integer |  |  | 0x50 |  | -- | -- | Action | verifies the integrity before activation; result can be (0) success, if the verification could be completed; (2) temporary-failure if the verification has not been completed; (250) other-reason if the verification failed.
4 | image_activate |  |  | integer |  |  | 0x58 |  | -- | -- | Action | activates the transferred and verified image; result can be (0) success, if the verification could be completed; (2) temporary-failure if the verification has not been completed; (250) other-reason if the verification failed.
| Image transfer activation scheduler | M | M |  | 22 | 0 |  | 0-0:15.0.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000F0002FF" | -- | -- | Get
2 | executed_script |  |  | script22 |  |  | 0x08 | {0-0:10.0.107.255,1} | -- | -- | Get, (Set) | activate image
3 | type |  |  | enum |  |  | 0x10 | 1 | -- | -- | Get, (Set) | 1 is mandatory (Other are optional. If only type 1 is supported Set is optional)
4 | execution_time |  |  | array[0..1](execution_time_date) |  |  | 0x18 |  | -- | -- | Get, Set | the execution can be disabled with writing empty array or {{"FFFFFFFF", "FFFFFFFFFF"}}
| Predefined Scripts - Image activation | M | M |  | 9 | 0 |  | 0-0:10.0.107.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000A006BFF" | -- | -- | Get
2 | scripts |  |  | scripts |  |  | 0x08 |  | -- | -- | (Get) | The attribute's access rights must be declared in CTI file. Allowed possibilities - no access or Get access
1 | execute |  |  | long_unsigned |  |  | 0x20 | 1 | -- | -- | Action | The activation of this scripts is performed by calling the execute() method to the script identifier 1 of the corresponding script object
| Active firmware identifier | M | M |  | 1 | 0 |  | 1-0:0.2.0.255 |  |  |  | If several FW instances are present inside the device, the B field is used for differentiation: 0=Metrologically relevant part of firmware 1=Application (metrologically non relevant part of firmware) 2=other parts (e.g. modem firmware)
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100000200FF" | -- | -- | Get
2 | value |  |  | octet_string |  |  | 0x08 |  | -- | -- | Get
| Active firmware signature | M | M |  | 1 | 0 |  | 1-0:0.2.8.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100000208FF" | -- | -- | Get
2 | value |  |  | octet_string |  |  | 0x08 |  | -- | -- | Get
| Active firmware identifier 1 | O | O |  | 1 | 0 |  | 1-1:0.2.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0101000200FF" | -- | -- | Get
2 | value |  |  | octet_string |  |  | 0x08 |  | -- | -- | Get
| Active firmware signature 1 | O | O |  | 1 | 0 |  | 1-1:0.2.8.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0101000208FF" | -- | -- | Get
2 | value |  |  | octet_string |  |  | 0x08 |  | -- | -- | Get
| Active firmware identifier 2 | O | O |  | 1 | 0 |  | 1-2:0.2.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0102000200FF" | -- | -- | Get
2 | value |  |  | octet_string |  |  | 0x08 |  | -- | -- | Get
| Active firmware signature 2 | O | O |  | 1 | 0 |  | 1-2:0.2.8.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0102000208FF" | -- | -- | Get
2 | value |  |  | octet_string |  |  | 0x08 |  | -- | -- | Get
Electricity related objects - Totals
| Active energy import (+A) | M | M |  | 3 | 0 |  | 1-0:1.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy export (−A) | M | M |  | 3 | 0 |  | 1-0:2.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy (¦+A¦+¦-A¦) Combined total | M | M |  | 3 | 0 |  | 1-0:15.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000F0800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy (¦+A¦-¦-A¦) Combined total | M | M |  | 3 | 0 |  | 1-0:16.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100100800FF" | -- | -- | Get
2 | value |  |  | double_long |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy QI (+Ri) | M | M |  | 3 | 0 |  | 1-0:5.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100050800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy QII (+Rc) | M | M |  | 3 | 0 |  | 1-0:6.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100060800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy QIII (-Ri) | M | M |  | 3 | 0 |  | 1-0:7.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100070800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy QIV (-Rc) | M | M |  | 3 | 0 |  | 1-0:8.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100080800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy import (+R) (QI+QII) | M | M |  | 3 | 0 |  | 1-0:3.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy export (-R) (QIII+QIV) | M | M |  | 3 | 0 |  | 1-0:4.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Apparent energy import (+VA) (QI+QIV) | O | O |  | 3 | 0 |  | 1-0:9.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,31} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Apparent energy export (-VA) (QII+QIII) | O | O |  | 3 | 0 |  | 1-0:10.8.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0800FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,31} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Electricity related objects - Rated registers | [10 empty] | Should be able to perform at least 4 tariffs.
| Active energy import (+A) rate 1 | M | M |  | 3 | 0 |  | 1-0:1.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy import (+A) rate 2 | M | M |  | 3 | 0 |  | 1-0:1.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy import (+A) rate 3 | M | M |  | 3 | 0 |  | 1-0:1.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy import (+A) rate 4 | M | M |  | 3 | 0 |  | 1-0:1.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy export (−A) rate 1 | M | M |  | 3 | 0 |  | 1-0:2.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy export (−A) rate 2 | M | M |  | 3 | 0 |  | 1-0:2.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy export (−A) rate 3 | M | M |  | 3 | 0 |  | 1-0:2.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy export (−A) rate 4 | M | M |  | 3 | 0 |  | 1-0:2.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (+R) rate 1 | M | M |  | 3 | 0 |  | 1-0:3.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (+R) rate 2 | M | M |  | 3 | 0 |  | 1-0:3.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (+R) rate 3 | M | M |  | 3 | 0 |  | 1-0:3.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (+R) rate 4 | M | M |  | 3 | 0 |  | 1-0:3.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (-R) rate 1 | M | M |  | 3 | 0 |  | 1-0:4.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (-R) rate 2 | M | M |  | 3 | 0 |  | 1-0:4.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (-R) rate 3 | M | M |  | 3 | 0 |  | 1-0:4.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (-R) rate 4 | M | M |  | 3 | 0 |  | 1-0:4.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QI) rate 1 | O | O |  | 3 | 0 |  | 1-0:5.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100050801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QI) rate 2 | O | O |  | 3 | 0 |  | 1-0:5.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100050802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QI) rate 3 | O | O |  | 3 | 0 |  | 1-0:5.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100050803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QI) rate 4 | O | O |  | 3 | 0 |  | 1-0:5.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100050804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QII) rate 1 | O | O |  | 3 | 0 |  | 1-0:6.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100060801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QII) rate 2 | O | O |  | 3 | 0 |  | 1-0:6.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100060802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QII) rate 3 | O | O |  | 3 | 0 |  | 1-0:6.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100060803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QII) rate 4 | O | O |  | 3 | 0 |  | 1-0:6.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100060804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QIII) rate 1 | O | O |  | 3 | 0 |  | 1-0:7.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100070801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QIII) rate 2 | O | O |  | 3 | 0 |  | 1-0:7.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100070802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QIII) rate 3 | O | O |  | 3 | 0 |  | 1-0:7.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100070803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QIII) rate 4 | O | O |  | 3 | 0 |  | 1-0:7.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100070804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QIV) rate 1 | O | O |  | 3 | 0 |  | 1-0:8.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100080801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QIV) rate 2 | O | O |  | 3 | 0 |  | 1-0:8.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100080802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QIV) rate 3 | O | O |  | 3 | 0 |  | 1-0:8.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100080803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Reactive energy (QIV) rate 4 | O | O |  | 3 | 0 |  | 1-0:8.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100080804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,32} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Apparent energy import (+VA) rate 1 | O | O |  | 3 | 0 |  | 1-0:9.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,31} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Apparent energy import (+VA) rate 2 | O | O |  | 3 | 0 |  | 1-0:9.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,31} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Apparent energy import (+VA) rate 3 | O | O |  | 3 | 0 |  | 1-0:9.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,31} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Apparent energy import (+VA) rate 4 | O | O |  | 3 | 0 |  | 1-0:9.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,31} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Apparent energy export (-VA) rate 1 | O | O |  | 3 | 0 |  | 1-0:10.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,31} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Apparent energy export (-VA) rate 2 | O | O |  | 3 | 0 |  | 1-0:10.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,31} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Apparent energy export (-VA) rate 3 | O | O |  | 3 | 0 |  | 1-0:10.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,31} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Apparent energy export (-VA) rate 4 | O | O |  | 3 | 0 |  | 1-0:10.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,31} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy Combined total (¦+A¦+¦-A¦) rate 1 | O | O |  | 3 | 0 |  | 1-0:15.8.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000F0801FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy Combined total (¦+A¦+¦-A¦) rate 2 | O | O |  | 3 | 0 |  | 1-0:15.8.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000F0802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy Combined total (¦+A¦+¦-A¦) rate 3 | O | O |  | 3 | 0 |  | 1-0:15.8.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000F0803FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Active energy Combined total (¦+A¦+¦-A¦) rate 4 | O | O |  | 3 | 0 |  | 1-0:15.8.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000F0804FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,30} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
Electricity related objects - Demand
| Demand Register 1 - Active energy import (+A) | M | M |  | 5 | 0 |  | 1-0:1.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010400FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | {0,27} | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 900 | -- | -- | Get, Set | Changing period of one instance will change the period of all instances automatically!
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 1 | -- | -- | Get, Set | Siliding demand optiona. Changing number_of_periods of one instance will change nunmber_of_periods of all instances automatically!
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Demand Register 2 - Active energy export (−A) | M | M |  | 5 | 0 |  | 1-0:2.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020400FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | {0,27} | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 900 | -- | -- | Get, Set | Changing period of one instance will change the period of all instances automatically!
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 1 | -- | -- | Get, Set | Siliding demand optiona. Changing number_of_periods of one instance will change nunmber_of_periods of all instances automatically!
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Demand Register 3 - Reactive energy import (+R) | M | M |  | 5 | 0 |  | 1-0:3.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030400FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | {0,29} | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 900 | -- | -- | Get, Set | Changing period of one instance will change the period of all instances automatically!
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 1 | -- | -- | Get, Set | Siliding demand optiona. Changing number_of_periods of one instance will change nunmber_of_periods of all instances automatically!
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Demand Register 4 - Reactive energy export (-R) | M | M |  | 5 | 0 |  | 1-0:4.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040400FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | {0,29} | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 900 | -- | -- | Get, Set | Changing period of one instance will change the period of all instances automatically!
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 1 | -- | -- | Get, Set | Siliding demand optiona. Changing number_of_periods of one instance will change nunmber_of_periods of all instances automatically!
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Demand Register 5 - Apparent energy import (+VA) | O | O |  | 5 | 0 |  | 1-0:9.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090400FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | {0,28} | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 900 | -- | -- | Get, Set | Changing period of one instance will change the period of all instances automatically!
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 1 | -- | -- | Get, Set | Siliding demand optiona. Changing number_of_periods of one instance will change nunmber_of_periods of all instances automatically!
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Demand Register 6 - Apparent energy export (-VA) | O | O |  | 5 | 0 |  | 1-0:10.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0400FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | {0,28} | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 900 | -- | -- | Get, Set | Changing period of one instance will change the period of all instances automatically!
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 1 | -- | -- | Get, Set | Siliding demand optiona. Changing number_of_periods of one instance will change nunmber_of_periods of all instances automatically!
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Last Average Demand Register 1 - Active energy import (+A) | O | O |  | 4 | 0 |  | 1-0:1.5.0.255 |  |  |  | For display purposes only
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010500FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Last Average Demand Register 2 - Active energy export (−A) | O | O |  | 4 | 0 |  | 1-0:2.5.0.255 |  |  |  | For display purposes only
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020500FF" | -- | -- | Get | For the display purpose only
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get | For the display purpose only
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get | For the display purpose only
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | For the display purpose only
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | For the display purpose only
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | -- | For the display purpose only
For the display purpose only
| Last Average Demand Register 3 - Reactive energy import (+R) | O | O |  | 4 | 0 |  | 1-0:3.5.0.255 |  |  |  | For display purposes only
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030500FF" | -- | -- | Get | For the display purpose only
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get | For the display purpose only
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get | For the display purpose only
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | For the display purpose only
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | For the display purpose only
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | -- | For the display purpose only
For the display purpose only
| Last Average Demand Register 4 - Reactive energy export (-R) | O | O |  | 4 | 0 |  | 1-0:4.5.0.255 |  |  |  | For display purposes only
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040500FF" | -- | -- | Get | For the display purpose only
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get | For the display purpose only
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get | For the display purpose only
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | For the display purpose only
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | For the display purpose only
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | -- | For the display purpose only
For the display purpose only
| Last Average Demand Register 5 - Apparent energy import (+VA) | O | O |  | 4 | 0 |  | 1-0:9.5.0.255 |  |  |  | For display purposes only
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090500FF" | -- | -- | Get | For the display purpose only
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get | For the display purpose only
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get | For the display purpose only
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | For the display purpose only
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | For the display purpose only
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | -- | For the display purpose only
For the display purpose only
| Last Average Demand Register 6 - Apparent energy export (-VA) | O | O |  | 4 | 0 |  | 1-0:10.5.0.255 |  |  |  | For display purposes only
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0500FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 1 - Active energy import (+A) | M | M |  | 4 | 0 |  | 1-0:1.6.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010600FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 2 - Active energy import (+A) - rate 1 | M | M |  | 4 | 0 |  | 1-0:1.6.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010601FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 3 - Active energy import (+A) - rate 2 | M | M |  | 4 | 0 |  | 1-0:1.6.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010602FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 4 - Active energy import (+A) - rate 3 | M | M |  | 4 | 0 |  | 1-0:1.6.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010603FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 5 - Active energy import (+A) - rate 4 | M | M |  | 4 | 0 |  | 1-0:1.6.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010604FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 6 - Active energy export (−A) | M | M |  | 4 | 0 |  | 1-0:2.6.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020600FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 7 - Active energy export (−A) - rate 1 | M | M |  | 4 | 0 |  | 1-0:2.6.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020601FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 8 - Active energy export (−A) - rate 2 | M | M |  | 4 | 0 |  | 1-0:2.6.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020602FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 9 - Active energy export (−A) - rate 3 | M | M |  | 4 | 0 |  | 1-0:2.6.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020603FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 10 - Active energy export (−A) - rate 4 | M | M |  | 4 | 0 |  | 1-0:2.6.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020604FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 11 - Reactive energy import (+R) | M | M |  | 4 | 0 |  | 1-0:3.6.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030600FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | not use; return 0
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 12 - Reactive energy import (+R) - rate 1 | M | M |  | 4 | 0 |  | 1-0:3.6.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030601FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | not use; return 0
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 13 - Reactive energy import (+R) - rate 2 | M | M |  | 4 | 0 |  | 1-0:3.6.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030602FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | not use; return 0
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 14 - Reactive energy import (+R) - rate 3 | M | M |  | 4 | 0 |  | 1-0:3.6.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030603FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | not use; return 0
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 15 - Reactive energy import (+R) - rate 4 | M | M |  | 4 | 0 |  | 1-0:3.6.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030604FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | not use; return 0
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 16 - Reactive energy export (-R) | M | M |  | 4 | 0 |  | 1-0:4.6.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040600FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | not use; return 0
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 17 - Reactive energy export (-R) - rate 1 | M | M |  | 4 | 0 |  | 1-0:4.6.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040601FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | not use; return 0
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 18 - Reactive energy export (-R) - rate 2 | M | M |  | 4 | 0 |  | 1-0:4.6.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040602FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | not use; return 0
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 19 - Reactive energy export (-R) - rate 3 | M | M |  | 4 | 0 |  | 1-0:4.6.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040603FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | not use; return 0
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 20 - Reactive energy export (-R) - rate 4 | M | M |  | 4 | 0 |  | 1-0:4.6.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040604FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get | not use; return 0
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 21 - Apparent energy import (+VA) | O | O |  | 4 | 0 |  | 1-0:9.6.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090600FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 22 - Apparent energy import (+VA) - rate 1 | O | O |  | 4 | 0 |  | 1-0:9.6.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090601FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 23 - Apparent energy import (+VA) - rate 2 | O | O |  | 4 | 0 |  | 1-0:9.6.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090602FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 24 - Apparent energy import (+VA) - rate 3 | O | O |  | 4 | 0 |  | 1-0:9.6.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090603FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 25 - Apparent energy import (+VA) - rate 4 | O | O |  | 4 | 0 |  | 1-0:9.6.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090604FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 26 - Apparent energy export (-VA) | O | O |  | 4 | 0 |  | 1-0:10.6.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0600FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 27 - Apparent energy export (-VA) - rate 1 | O | O |  | 4 | 0 |  | 1-0:10.6.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0601FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 28 - Apparent energy export (-VA) - rate 2 | O | O |  | 4 | 0 |  | 1-0:10.6.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0602FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 29 - Apparent energy export (-VA) - rate 3 | O | O |  | 4 | 0 |  | 1-0:10.6.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0603FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Maximum Demand Register 30 - Apparent energy export (-VA) - rate 4 | O | O |  | 4 | 0 |  | 1-0:10.6.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0604FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
Electricity related objects - Profiles
| Profile status - Load profile with period 1 | M | M |  | 1 | 0 |  | 0-0:96.10.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600A01FF" | -- | -- | Get
2 | status |  |  | unsigned |  |  | 0x08 |  | -- | -- | Get | bitmask :: {PDN,reserved,CAD,reserved,DST,DNV,CIV,ERR}
| Load profile with period 1 i.e. General Load Profile | M | M |  | 7 | 1 |  | 1-0:99.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100630100FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range and entry
3 | capture_objects |  |  | array[2..*](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0},{1,0-0:96.10.1.255,2,0}, {3,1-0:1.8.0.255,2,0}, {3,1-0:2.8.0.255,2,0}, ...} | -- | -- | Get, Set | clock;AMR profile status; +A;−A
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | choice(300, 600, 900, 1800, 3600) | -- | -- | Get, Set | 15 minutes
5 | sort_method |  |  | enum |  |  | 0x20 | choice(1,4) | -- | -- | Get | unsorted (FIFO) or sorted (smallest)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | choice({*,*-*:*.*.*.*,*,*}, {8,0-0:1.0.0.255,2,0}) | -- | -- | Get | unsorted or sorted by clock depending on choice in attr. sort_method i.e. if sort_method=sorted then sort_object=0-0:1.0.0.255
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [960..*] | -- | -- | Get, (Set) | ≥10 days, optional set to restrict maximum capacity according to national laws
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
| Profile status - Load profile with period 2 | M | M |  | 1 | 0 |  | 0-0:96.10.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600A02FF" | -- | -- | Get
2 | status |  |  | unsigned |  |  | 0x08 |  | -- | -- | Get | bitmask :: {PDN,reserved,CAD,reserved,DST,DNV,CIV,ERR}
| Load profile with period 2 i.e. Daily Values Profile | M | M |  | 7 | 1 |  | 1-0:99.2.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100630200FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range and entry
3 | capture_objects |  |  | array[2..*](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0},{1,0-0:96.10.2.255,2,0},{3,1-0:1.8.*.255,2,0}, ...} | -- | -- | Get, Set | clock;AMR profile status; choice amongst rated registers, etc.
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | choice(86400, 300, 600, 900, 1800, 3600) | -- | -- | Get, Set | daily
5 | sort_method |  |  | enum |  |  | 0x20 | choice(1,4) | -- | -- | Get | unsorted (FIFO) or sorted (smallest)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | choice({*,*-*:*.*.*.*,*,*}, {8,0-0:1.0.0.255,2,0}) | -- | -- | Get | unsorted or sorted by clock depending on choice in attr. sort_method i.e. if sort_method=sorted then sort_object=0-0:1.0.0.255
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [10..*] | -- | -- | Get, (Set) | ≥10 days, optional set to restrict maximum capacity according to national laws
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
Electricity related objects - PQ, monitored values
| Number of power failures in any phase | M | M |  | 1 | 0 |  | 0-0:96.7.21.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600715FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
| Number of long power failures in any phase | M | M |  | 1 | 0 |  | 0-0:96.7.9.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600709FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
| Time threshold for long power failure | M | M |  | 3 | 0 |  | 0-0:96.7.20.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600714FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 | 180 | -- | Set | Get, Set
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Duration of last long power failure in any phase | M | M |  | 3 | 0 |  | 0-0:96.7.19.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600713FF" | -- | -- | Get
2 | value |  |  | choice(long_unsigned, double_long_unsigned) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Threshold for voltage sag | M | M |  | 3 | 0 |  | 1-0:12.31.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000C1F00FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 | 207 | -- | Set | Get, Set
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,35} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Time threshold for voltage sag | M | M |  | 3 | 0 |  | 1-0:12.43.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000C2B00FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 | 30 | -- | Set | Get, Set
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Number of voltage sags in phase L1 | M | M |  | 1 | 0 |  | 1-0:32.32.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100202000FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
| Number of voltage sags in phase L2 | NA | M |  | 1 | 0 |  | 1-0:52.32.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100342000FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
| Number of voltage sags in phase L3 | NA | M |  | 1 | 0 |  | 1-0:72.32.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100482000FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
| Duration of last voltage sag in phase L1 | M | M |  | 3 | 0 |  | 1-0:32.33.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100202100FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Duration of last voltage sag in phase L2 | NA | M |  | 3 | 0 |  | 1-0:52.33.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100342100FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Duration of last voltage sag in phase L3 | NA | M |  | 3 | 0 |  | 1-0:72.33.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100482100FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Magnitude of last voltage sag in phase L1 | M | M |  | 3 | 0 |  | 1-0:32.34.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100202200FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,35} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Magnitude of last voltage sag in phase L2 | NA | M |  | 3 | 0 |  | 1-0:52.34.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100342200FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,35} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Magnitude of last voltage sag in phase L3 | NA | M |  | 3 | 0 |  | 1-0:72.34.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100482200FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,35} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Threshold for voltage swell | M | M |  | 3 | 0 |  | 1-0:12.35.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000C2300FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 | 253 | -- | Set | Get, Set
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,35} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Time threshold for voltage swell | M | M |  | 3 | 0 |  | 1-0:12.44.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000C2C00FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 | 30 | -- | Set | Get, Set
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Number of voltage swells in phase L1 | M | M |  | 1 | 0 |  | 1-0:32.36.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100202400FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
| Number of voltage swells in phase L2 | NA | M |  | 1 | 0 |  | 1-0:52.36.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100342400FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
| Number of voltage swells in phase L3 | NA | M |  | 1 | 0 |  | 1-0:72.36.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100482400FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
| Duration of last voltage swell in phase L1 | M | M |  | 3 | 0 |  | 1-0:32.37.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100202500FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Duration of last voltage swell in phase L2 | NA | M |  | 3 | 0 |  | 1-0:52.37.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100342500FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Duration of last voltage swell in phase L3 | NA | M |  | 3 | 0 |  | 1-0:72.37.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100482500FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Magnitude of last voltage swell in phase L1 | M | M |  | 3 | 0 |  | 1-0:32.38.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100202600FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,35} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Magnitude of last voltage swell in phase L2 | NA | M |  | 3 | 0 |  | 1-0:52.38.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100342600FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,35} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Magnitude of last voltage swell in phase L3 | NA | M |  | 3 | 0 |  | 1-0:72.38.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100482600FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,35} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Threshold for missing voltage (voltage cut) | M | M |  | 3 | 0 |  | 1-0:12.39.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000C2700FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 | 103 | -- | Set | Get, Set
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,35} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Time threshold for voltage cut | M | M |  | 3 | 0 |  | 1-0:12.45.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000C2D00FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 | 30 | -- | Set | Get, Set
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Power Failure Event Log | M | M |  | 7 | 1 |  | 1-0:99.97.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100636100FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {3,0-0:96.7.19.255,2,0}} | -- | -- | Get, (Set) | clock;duration of long power failures in any phase
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [10..*] | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x58 |  | -- | -- | Action
| Event Object - Power Quality Log | M | M |  | 1 | 0 |  | 0-0:96.11.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600B04FF" | -- | -- | Get
2 | value |  |  | choice(enum, long_unsigned) |  |  | 0x08 |  | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| Power Quality Log | M | M |  | 7 | 1 |  | 0-0:99.98.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000636204FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.4.255,2,0}} | -- | -- | Get, (Set) | clock;event code
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [100..*] | -- | -- | Get
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
| Instantaneous voltage L1 | M | M |  | 3 | 0 |  | 1-0:32.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100200700FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,35},{-1,35}) | -- | -- | Get | scaler=0 or-1, unit=V resolution: 0 or 0.0 V
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Average voltage L1 | M | M |  | 3 | 0 |  | 1-0:32.24.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100201800FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get | 10 minutes average voltage
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,35},{-1,35}) | -- | -- | Get | scaler=0 or-1, unit=V resolution: 0 or 0.0 V
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous current L1 | M | M |  | 3 | 0 |  | 1-0:31.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01001F0700FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,33},{-1,33},{-2,33}) | -- | -- | Get | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Sliding Average current L1 (for fuse supervision) | M-D | M-D |  | 5 | 0 |  | 1-0:31.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01001F0400FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | choice({0,33},{-1,33},{-2,33}) | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 1 | -- | -- | Get
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 90 | -- | -- | Get, Set
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Instantaneous voltage L2 | NA | M |  | 3 | 0 |  | 1-0:52.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100340700FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,35},{-1,35}) | -- | -- | Get | scaler=0 or-1, unit=V resolution: 0 or 0.0 V
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Average voltage L2 | NA | M |  | 3 | 0 |  | 1-0:52.24.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100341800FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get | 10 minutes average voltage
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,35},{-1,35}) | -- | -- | Get | scaler=0 or-1, unit=V resolution: 0 or 0.0 V
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous current L2 | NA | M |  | 3 | 0 |  | 1-0:51.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100330700FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,33},{-1,33},{-2,33}) | -- | -- | Get | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Sliding Average current L2 (for fuse supervision) | NA | M-D |  | 5 | 0 |  | 1-0:51.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100330400FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | choice({0,33},{-1,33},{-2,33}) | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 1 | -- | -- | Get
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 90 | -- | -- | Get, Set
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Instantaneous voltage L3 | NA | M |  | 3 | 0 |  | 1-0:72.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100480700FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,35},{-1,35}) | -- | -- | Get | scaler=0 or-1, unit=V resolution: 0 or 0.0 V
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Average voltage L3 | NA | M |  | 3 | 0 |  | 1-0:72.24.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100481800FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get | 10 minutes average voltage
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,35},{-1,35}) | -- | -- | Get | scaler=0 or-1, unit=V resolution: 0 or 0.0 V
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous current L3 | NA | M |  | 3 | 0 |  | 1-0:71.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100470700FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,33},{-1,33},{-2,33}) | -- | -- | Get | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Sliding Average current L3 (for fuse supervision) | NA | M-D |  | 5 | 0 |  | 1-0:71.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100470400FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | choice({0,33},{-1,33},{-2,33}) | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 1 | -- | -- | Get
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 90 | -- | -- | Get, Set
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Instantaneous current (sum over all phases) | M | M |  | 3 | 0 |  | 1-0:90.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01005A0700FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get | total current (sum of all phases)
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,33},{-1,33},{-2,33}) | -- | -- | Get | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous net frequency; any phase | O | O |  | 3 | 0 |  | 1-0:14.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000E0700FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | choice({0,44},{-1,44},{-2,44}) | -- | -- | Get | scaler=0,-1 or-2, unit=Hz resolution: 0, 0.0 or 0.00 Hz
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous active power (¦+A¦+¦-A¦) | M | M |  | 3 | 0 |  | 1-0:15.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000F0700FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get | sum of all phases: ¦QI+QIV¦+¦QII+QIII¦
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous active import power (+A) | M | M |  | 3 | 0 |  | 1-0:1.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100010700FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous active export power (-A) | M | M |  | 3 | 0 |  | 1-0:2.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100020700FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,27} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous reactive import power (+R) | M | M |  | 3 | 0 |  | 1-0:3.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100030700FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous reactive export power (-R) | M | M |  | 3 | 0 |  | 1-0:4.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100040700FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,29} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous apparent import power (+VA) | O | O |  | 3 | 0 |  | 1-0:9.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100090700FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Instantaneous apparent export power (-VA) | O | O |  | 3 | 0 |  | 1-0:10.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000A0700FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,28} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Average Import Power (+A) | M-D | M-D |  | 5 | 0 |  | 1-0:1.24.0.255 |  |  |  | Sliding demand with its own period
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100011800FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | {0,27} | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 60 | -- | -- | Get
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 15 | -- | -- | Get, Set
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Average Net Power (¦+A¦-¦-A¦) | O | O |  | 5 | 0 |  | 1-0:16.24.0.255 |  |  |  | Sliding demand with its own period
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100101800FF" | -- | -- | Get
2 | current_average_value |  |  | double_long |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | {0,27} | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 60 | -- | -- | Get
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 15 | -- | -- | Get, Set
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Average Total Power (¦+A¦+¦-A¦) | M-D | M-D |  | 5 | 0 |  | 1-0:15.24.0.255 |  |  |  | Sliding demand with its own period
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000F1800FF" | -- | -- | Get
2 | current_average_value |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | last_average_value |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | scaler_unit |  |  | scal_unit_type |  |  | 0x18 | {0,27} | -- | -- | Get
5 | status |  |  | unsigned |  |  | 0x20 | 0 | -- | -- | Get
6 | capture_time |  |  | octet_string |  |  | 0x28 |  | -- | -- | Get
7 | start_time_current |  |  | octet_string |  |  | 0x30 |  | -- | -- | Get
8 | period |  |  | double_long_unsigned |  |  | 0x38 | 60 | -- | -- | Get
9 | number_of_periods |  |  | long_unsigned |  |  | 0x40 | 15 | -- | -- | Get, Set
1 | reset | [5 empty] | 0x48 |  | -- | -- | --
2 | next_period | [5 empty] | 0x50 |  | -- | -- | --
| Instantaneous Power factor (+A/+VA) | O | O |  | 3 | 0 |  | 1-0:13.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000D0700FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {-3,255} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
| Last Average Power factor (+A/+VA) | O | O |  | 4 | 0 |  | 1-0:13.5.0.255 |  |  |  | For display purposes only
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000D0500FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {-3,255} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Minimum Power factor (+A/+VA) | O | O |  | 4 | 0 |  | 1-0:13.3.0.255 |  |  |  | For display purposes only
1 | logical_name |  |  | octet_string[6] |  |  |  | "01000D0300FF" | -- | -- | Get
2 | value |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {-3,255} | -- | -- | Get
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x38 |  | -- | -- | --
| Measurement Period 3 for Instantaneous values | O | O |  | 3 | 0 |  | 1-0:0.8.2.255 |  |  |  | Used with simple average scheme (see IC3, D=24). If object not used period is considered as implicit!
1 | logical_name |  |  | octet_string[6] |  |  |  | "0100000802FF" | -- | -- | Get
2 | value |  |  | double_long_unsigned |  |  | 0x08 | 600 | -- | Set | Get, Set
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 | {0,7} | -- | -- | Get
1 | reset | [5 empty] | 0x28 |  | -- | -- | --
Local communication - M-Bus
| M-Bus master port setup 1 | M-M | M-M |  | 74 | 0 |  | 0-0:24.6.0.255 |  |  |  | Wired M-Bus port setup
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000180600FF" | -- | -- | Get
2 | comm_speed |  |  | enum |  |  | 0x08 | 3 | -- | -- | Get | 3== 2400 bps fix
| M-Bus master port setup 2 | O | O |  | 74 | 0 |  | 0-1:24.6.0.255 |  |  |  | Wireless M-Bus port setup
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001180600FF" | -- | -- | Get
2 | comm_speed |  |  | enum |  |  | 0x08 |  | -- | -- | Get | (0) 300 bps, (1) 600 bps, (2) 1200 bps, (3) 2400 bps, (4) 4800 bps, (5) 9600 bps, (6) 19200 bps...
| M-Bus client channel 1 | M-M | M-M |  | 72 | 0 |  | 0-1:24.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001180100FF" | -- | -- | Get
2 | mbus_port_reference |  |  | octet_string[6] |  |  | 0x08 | choice(0-0:24.6.0.255, 0-1:24.6.0.255) | -- | -- | Get, Set
3 | capture_definition |  |  | array |  |  | 0x10 |  | -- | -- | Get, Set
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 |  | -- | Set | Get, Set
5 | primary_address |  |  | unsigned |  |  | 0x20 |  | -- | -- | Get, Set
6 | identification_number |  |  | double_long_unsigned |  |  | 0x28 |  | -- | -- | Get
7 | manufacturer_id |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | version |  |  | unsigned |  |  | 0x38 |  | -- | -- | Get
9 | device_type |  |  | unsigned |  |  | 0x40 |  | -- | -- | Get
10 | access_number |  |  | unsigned |  |  | 0x48 |  | -- | -- | Get
11 | status |  |  | unsigned |  |  | 0x50 |  | -- | -- | Get
12 | alarm |  |  | unsigned |  |  | 0x58 |  | -- | -- | Get
1 | slave_install |  |  | unsigned |  |  | 0x68 |  | -- | -- | Action
2 | slave_deinstall |  |  | unsigned |  |  | 0x70 |  | -- | -- | Action
3 | capture |  |  | integer |  |  | 0x78 |  | -- | -- | (Action)
4 | reset_alarm |  |  | integer |  |  | 0x80 |  | -- | -- | (Action)
5 | synchronize_clock |  |  | integer |  |  | 0x88 |  | -- | -- | (Action)
6 | data_send |  |  | array |  |  | 0x90 |  | -- | -- | (Action)
7 | set_encryption_key |  |  | octet_string |  |  | 0x98 |  | -- | -- | Action
8 | transfer_key |  |  | octet_string |  |  | 0xA0 |  | -- | -- | Action
| M-Bus client channel 2 | M-M | M-M |  | 72 | 0 |  | 0-2:24.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002180100FF" | -- | -- | Get
2 | mbus_port_reference |  |  | octet_string[6] |  |  | 0x08 | choice(0-0:24.6.0.255, 0-1:24.6.0.255) | -- | -- | Get, Set
3 | capture_definition |  |  | array |  |  | 0x10 |  | -- | -- | Get, Set
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 |  | -- | Set | Get, Set
5 | primary_address |  |  | unsigned |  |  | 0x20 |  | -- | -- | Get, Set
6 | identification_number |  |  | double_long_unsigned |  |  | 0x28 |  | -- | -- | Get
7 | manufacturer_id |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | version |  |  | unsigned |  |  | 0x38 |  | -- | -- | Get
9 | device_type |  |  | unsigned |  |  | 0x40 |  | -- | -- | Get
10 | access_number |  |  | unsigned |  |  | 0x48 |  | -- | -- | Get
11 | status |  |  | unsigned |  |  | 0x50 |  | -- | -- | Get
12 | alarm |  |  | unsigned |  |  | 0x58 |  | -- | -- | Get
1 | slave_install |  |  | unsigned |  |  | 0x68 |  | -- | -- | Action
2 | slave_deinstall |  |  | unsigned |  |  | 0x70 |  | -- | -- | Action
3 | capture |  |  | integer |  |  | 0x78 |  | -- | -- | (Action)
4 | reset_alarm |  |  | integer |  |  | 0x80 |  | -- | -- | (Action)
5 | synchronize_clock |  |  | integer |  |  | 0x88 |  | -- | -- | (Action)
6 | data_send |  |  | array |  |  | 0x90 |  | -- | -- | (Action)
7 | set_encryption_key |  |  | octet_string |  |  | 0x98 |  | -- | -- | Action
8 | transfer_key |  |  | octet_string |  |  | 0xA0 |  | -- | -- | Action
| M-Bus client channel 3 | M-M | M-M |  | 72 | 0 |  | 0-3:24.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003180100FF" | -- | -- | Get
2 | mbus_port_reference |  |  | octet_string[6] |  |  | 0x08 | choice(0-0:24.6.0.255, 0-1:24.6.0.255) | -- | -- | Get, Set
3 | capture_definition |  |  | array |  |  | 0x10 |  | -- | -- | Get, Set
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 |  | -- | Set | Get, Set
5 | primary_address |  |  | unsigned |  |  | 0x20 |  | -- | -- | Get, Set
6 | identification_number |  |  | double_long_unsigned |  |  | 0x28 |  | -- | -- | Get
7 | manufacturer_id |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | version |  |  | unsigned |  |  | 0x38 |  | -- | -- | Get
9 | device_type |  |  | unsigned |  |  | 0x40 |  | -- | -- | Get
10 | access_number |  |  | unsigned |  |  | 0x48 |  | -- | -- | Get
11 | status |  |  | unsigned |  |  | 0x50 |  | -- | -- | Get
12 | alarm |  |  | unsigned |  |  | 0x58 |  | -- | -- | Get
1 | slave_install |  |  | unsigned |  |  | 0x68 |  | -- | -- | Action
2 | slave_deinstall |  |  | unsigned |  |  | 0x70 |  | -- | -- | Action
3 | capture |  |  | integer |  |  | 0x78 |  | -- | -- | (Action)
4 | reset_alarm |  |  | integer |  |  | 0x80 |  | -- | -- | (Action)
5 | synchronize_clock |  |  | integer |  |  | 0x88 |  | -- | -- | (Action)
6 | data_send |  |  | array |  |  | 0x90 |  | -- | -- | (Action)
7 | set_encryption_key |  |  | octet_string |  |  | 0x98 |  | -- | -- | Action
8 | transfer_key |  |  | octet_string |  |  | 0xA0 |  | -- | -- | Action
| M-Bus client channel 4 | M-M | M-M |  | 72 | 0 |  | 0-4:24.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004180100FF" | -- | -- | Get
2 | mbus_port_reference |  |  | octet_string[6] |  |  | 0x08 | choice(0-0:24.6.0.255, 0-1:24.6.0.255) | -- | -- | Get, Set
3 | capture_definition |  |  | array |  |  | 0x10 |  | -- | -- | Get, Set
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 |  | -- | Set | Get, Set
5 | primary_address |  |  | unsigned |  |  | 0x20 |  | -- | -- | Get, Set
6 | identification_number |  |  | double_long_unsigned |  |  | 0x28 |  | -- | -- | Get
7 | manufacturer_id |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | version |  |  | unsigned |  |  | 0x38 |  | -- | -- | Get
9 | device_type |  |  | unsigned |  |  | 0x40 |  | -- | -- | Get
10 | access_number |  |  | unsigned |  |  | 0x48 |  | -- | -- | Get
11 | status |  |  | unsigned |  |  | 0x50 |  | -- | -- | Get
12 | alarm |  |  | unsigned |  |  | 0x58 |  | -- | -- | Get
1 | slave_install |  |  | unsigned |  |  | 0x68 |  | -- | -- | Action
2 | slave_deinstall |  |  | unsigned |  |  | 0x70 |  | -- | -- | Action
3 | capture |  |  | integer |  |  | 0x78 |  | -- | -- | (Action)
4 | reset_alarm |  |  | integer |  |  | 0x80 |  | -- | -- | (Action)
5 | synchronize_clock |  |  | integer |  |  | 0x88 |  | -- | -- | (Action)
6 | data_send |  |  | array |  |  | 0x90 |  | -- | -- | (Action)
7 | set_encryption_key |  |  | octet_string |  |  | 0x98 |  | -- | -- | Action
8 | transfer_key |  |  | octet_string |  |  | 0xA0 |  | -- | -- | Action
| M-Bus Value channel 1, instance 1 | M-M | M-M |  | 4 | 0 |  | 0-1:24.2.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001180201FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 1, instance 2 | M-M | M-M |  | 4 | 0 |  | 0-1:24.2.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001180202FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 1, instance 3 | M-M | M-M |  | 4 | 0 |  | 0-1:24.2.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001180203FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 1, instance 4 | M-M | M-M |  | 4 | 0 |  | 0-1:24.2.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001180204FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 2, instance 1 | M-M | M-M |  | 4 | 0 |  | 0-2:24.2.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002180201FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 2, instance 2 | M-M | M-M |  | 4 | 0 |  | 0-2:24.2.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002180202FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 2, instance 3 | M-M | M-M |  | 4 | 0 |  | 0-2:24.2.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002180203FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 2, instance 4 | M-M | M-M |  | 4 | 0 |  | 0-2:24.2.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002180204FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 3, instance 1 | M-M | M-M |  | 4 | 0 |  | 0-3:24.2.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003180201FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 3, instance 2 | M-M | M-M |  | 4 | 0 |  | 0-3:24.2.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003180202FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 3, instance 3 | M-M | M-M |  | 4 | 0 |  | 0-3:24.2.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003180203FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 3, instance 4 | M-M | M-M |  | 4 | 0 |  | 0-3:24.2.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003180204FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 4, instance 1 | M-M | M-M |  | 4 | 0 |  | 0-4:24.2.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004180201FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 4, instance 2 | M-M | M-M |  | 4 | 0 |  | 0-4:24.2.2.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004180202FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 4, instance 3 | M-M | M-M |  | 4 | 0 |  | 0-4:24.2.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004180203FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Value channel 4, instance 4 | M-M | M-M |  | 4 | 0 |  | 0-4:24.2.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004180204FF" | -- | -- | Get
2 | value |  |  | choice(double_long,double_long_unsigned,octet_string) |  |  | 0x08 |  | -- | -- | Get
3 | scaler_unit |  |  | scal_unit_type |  |  | 0x10 |  | -- | -- | Get, (Set)
4 | status |  |  | unsigned |  |  | 0x18 |  | -- | -- | Get
5 | capture_time |  |  | octet_string |  |  | 0x20 |  | -- | -- | Get | time of last successful readout; format same as clock.time
1 | reset | [5 empty] | 0x38 |  | -- | -- | (Action)
| M-Bus Device ID 1 channel 1 | M-M | M-M |  | 1 | 0 |  | 0-1:96.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001600100FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get, Set
| M-Bus Device ID 1 channel 2 | M-M | M-M |  | 1 | 0 |  | 0-2:96.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002600100FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get, Set
| M-Bus Device ID 1 channel 3 | M-M | M-M |  | 1 | 0 |  | 0-3:96.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003600100FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get, Set
| M-Bus Device ID 1 channel 4 | M-M | M-M |  | 1 | 0 |  | 0-4:96.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004600100FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get, Set
| M-Bus Device ID 2 channel 1 | M-M | M-M |  | 1 | 0 |  | 0-1:96.1.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001600101FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get, Set
| M-Bus Device ID 2 channel 2 | M-M | M-M |  | 1 | 0 |  | 0-2:96.1.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002600101FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get, Set
| M-Bus Device ID 2 channel 3 | M-M | M-M |  | 1 | 0 |  | 0-3:96.1.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003600101FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get, Set
| M-Bus Device ID 2 channel 4 | M-M | M-M |  | 1 | 0 |  | 0-4:96.1.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004600101FF" | -- | -- | Get
2 | value |  |  | octet_string[0..48] |  |  | 0x08 |  | -- | -- | Get, Set
| Profile status for M-Bus Master Load profile 1 | M-M | M-M |  | 1 | 0 |  | 0-1:96.10.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001600A03FF" | -- | -- | Get
2 | status |  |  | unsigned |  |  | 0x08 |  | -- | -- | Get
| Profile status for M-Bus Master Load profile 2 | M-M | M-M |  | 1 | 0 |  | 0-2:96.10.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002600A03FF" | -- | -- | Get
2 | status |  |  | unsigned |  |  | 0x08 |  | -- | -- | Get
| Profile status for M-Bus Master Load profile 3 | M-M | M-M |  | 1 | 0 |  | 0-3:96.10.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003600A03FF" | -- | -- | Get
2 | status |  |  | unsigned |  |  | 0x08 |  | -- | -- | Get
| Profile status for M-Bus Master Load profile 4 | M-M | M-M |  | 1 | 0 |  | 0-4:96.10.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004600A03FF" | -- | -- | Get
2 | status |  |  | unsigned |  |  | 0x08 |  | -- | -- | Get
| M-Bus Master Load profile for channel 1 | M-M | M-M |  | 7 | 1 |  | 0-1:24.3.0.255 |  |  |  | Hourly interval readings of M-Bus devices
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001180300FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range and entry
3 | capture_objects |  |  | array[2..*](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1, 0-1:96.10.3.255,2,0}, {4, 0-1:24.2.[1..4].255,2,0}, {4, 0-1:24.2.[1..4].255,2,0}, {4, 0-1:24.2.[1..4].255,2,0}, {4, 0-1:24.2.[1..4].255,2,0}, ...} | -- | -- | Get, Set | clock;AMR status; M-Bus Master value object;
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 3600 | -- | -- | Get, Set | every hour
5 | sort_method |  |  | enum |  |  | 0x20 | choice(1,4) | -- | -- | Get | unsorted (FIFO) or sorted (smallest)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | choice({*,*-*:*.*.*.*,*,*}, {8,0-0:1.0.0.255,2,0}) | -- | -- | Get | unsorted or sorted by clock depending on choice in attr. sort_method i.e. if sort_method=sorted then sort_object=0-0:1.0.0.255
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [240..*] | -- | -- | Get | ≥10 days, optional set to restrict maximum capacity according to national laws
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
| M-Bus Master Load profile for channel 2 | M-M | M-M |  | 7 | 1 |  | 0-2:24.3.0.255 |  |  |  | Hourly interval readings of M-Bus devices
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002180300FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range and entry
3 | capture_objects |  |  | array[2..*](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1, 0-2:96.10.3.255,2,0}, {4, 0-2:24.2.[1..4].255,2,0}, {4, 0-2:24.2.[1..4].255,2,0}, {4, 0-2:24.2.[1..4].255,2,0}, {4, 0-2:24.2.[1..4].255,2,0}, ...} | -- | -- | Get, Set | clock;AMR status; M-Bus Master value object;
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 3600 | -- | -- | Get, Set | every hour
5 | sort_method |  |  | enum |  |  | 0x20 | choice(1,4) | -- | -- | Get | unsorted (FIFO) or sorted (smallest)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | choice({*,*-*:*.*.*.*,*,*}, {8,0-0:1.0.0.255,2,0}) | -- | -- | Get | unsorted or sorted by clock depending on choice in attr. sort_method i.e. if sort_method=sorted then sort_object=0-0:1.0.0.255
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [240..*] | -- | -- | Get | ≥10 days, optional set to restrict maximum capacity according to national laws
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
| M-Bus Master Load profile for channel 3 | M-M | M-M |  | 7 | 1 |  | 0-3:24.3.0.255 |  |  |  | Hourly interval readings of M-Bus devices
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003180300FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range and entry
3 | capture_objects |  |  | array[2..*](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1, 0-3:96.10.3.255,2,0}, {4, 0-3:24.2.[1..4].255,2,0}, {4, 0-3:24.2.[1..4].255,2,0}, {4, 0-3:24.2.[1..4].255,2,0}, {4, 0-3:24.2.[1..4].255,2,0}, ...} | -- | -- | Get, Set | clock;AMR status; M-Bus Master value object;
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 3600 | -- | -- | Get, Set | every hour
5 | sort_method |  |  | enum |  |  | 0x20 | choice(1,4) | -- | -- | Get | unsorted (FIFO) or sorted (smallest)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | choice({*,*-*:*.*.*.*,*,*}, {8,0-0:1.0.0.255,2,0}) | -- | -- | Get | unsorted or sorted by clock depending on choice in attr. sort_method i.e. if sort_method=sorted then sort_object=0-0:1.0.0.255
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [240..*] | -- | -- | Get | ≥10 days, optional set to restrict maximum capacity according to national laws
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
| M-Bus Master Load profile for channel 4 | M-M | M-M |  | 7 | 1 |  | 0-4:24.3.0.255 |  |  |  | Hourly interval readings of M-Bus devices
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004180300FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range and entry
3 | capture_objects |  |  | array[2..*](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1, 0-4:96.10.3.255,2,0}, {4, 0-4:24.2.[1..4].255,2,0}, {4, 0-4:24.2.[1..4].255,2,0}, {4, 0-4:24.2.[1..4].255,2,0}, {4, 0-4:24.2.[1..4].255,2,0}, ...} | -- | -- | Get, Set | clock;AMR status; M-Bus Master value object;
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 3600 | -- | -- | Get, Set | every hour
5 | sort_method |  |  | enum |  |  | 0x20 | choice(1,4) | -- | -- | Get | unsorted (FIFO) or sorted (smallest)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | choice({*,*-*:*.*.*.*,*,*}, {8,0-0:1.0.0.255,2,0}) | -- | -- | Get | unsorted or sorted by clock depending on choice in attr. sort_method i.e. if sort_method=sorted then sort_object=0-0:1.0.0.255
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [240..*] | -- | -- | Get | ≥10 days, optional set to restrict maximum capacity according to national laws
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
| M-Bus Master Disconnect control object 1 | M-M | M-M |  | 70 | 0 |  | 0-1:24.4.0.255 |  |  |  | Controls the opening and closing of an M-Bus disconnector (e.g. gas valve)
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001180400FF" | -- | -- | Get
2 | output_state |  |  | boolean |  |  | 0x08 |  | -- | -- | Get
3 | control_state |  |  | enum |  |  | 0x10 |  | -- | -- | Get
4 | control_mode |  |  | enum |  |  | 0x18 |  | -- | Set | Get, Set
1 | remote_disconnect |  |  | integer |  |  | 0x20 |  | -- | -- | Action
2 | remote_connect |  |  | integer |  |  | 0x28 |  | -- | -- | Action
| M-Bus Master Disconnect control object 2 | M-M | M-M |  | 70 | 0 |  | 0-2:24.4.0.255 |  |  |  | Controls the opening and closing of an M-Bus disconnector (e.g. gas valve)
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002180400FF" | -- | -- | Get
2 | output_state |  |  | boolean |  |  | 0x08 |  | -- | -- | Get
3 | control_state |  |  | enum |  |  | 0x10 |  | -- | -- | Get
4 | control_mode |  |  | enum |  |  | 0x18 |  | -- | Set | Get, Set
1 | remote_disconnect |  |  | integer |  |  | 0x20 |  | -- | -- | Action
2 | remote_connect |  |  | integer |  |  | 0x28 |  | -- | -- | Action
| M-Bus Master Disconnect control object 3 | M-M | M-M |  | 70 | 0 |  | 0-3:24.4.0.255 |  |  |  | Controls the opening and closing of an M-Bus disconnector (e.g. gas valve)
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003180400FF" | -- | -- | Get
2 | output_state |  |  | boolean |  |  | 0x08 |  | -- | -- | Get
3 | control_state |  |  | enum |  |  | 0x10 |  | -- | -- | Get
4 | control_mode |  |  | enum |  |  | 0x18 |  | -- | Set | Get, Set
1 | remote_disconnect |  |  | integer |  |  | 0x20 |  | -- | -- | Action
2 | remote_connect |  |  | integer |  |  | 0x28 |  | -- | -- | Action
| M-Bus Master Disconnect control object 4 | M-M | M-M |  | 70 | 0 |  | 0-4:24.4.0.255 |  |  |  | Controls the opening and closing of an M-Bus disconnector (e.g. gas valve)
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004180400FF" | -- | -- | Get
2 | output_state |  |  | boolean |  |  | 0x08 |  | -- | -- | Get
3 | control_state |  |  | enum |  |  | 0x10 |  | -- | -- | Get
4 | control_mode |  |  | enum |  |  | 0x18 |  | -- | Set | Get, Set
1 | remote_disconnect |  |  | integer |  |  | 0x20 |  | -- | -- | Action
2 | remote_connect |  |  | integer |  |  | 0x28 |  | -- | -- | Action
| M-Bus Disconnect control scheduler | M-M | M-M |  | 22 | 0 |  | 0-1:15.0.1.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00010F0001FF" | -- | -- | Get
2 | executed_script |  |  | script22 |  |  | 0x08 | {0-1:10.0.106.255, [1..16]} | -- | -- | Get, Set
3 | type |  |  | enum |  |  | 0x10 | 1 | -- | -- | Get, (Set) | 1 is mandatory (Other are optional. If only type 1 is supported Set is optional)
4 | execution_time |  |  | array[0..1](execution_time_date) |  |  | 0x18 | {{"FFFFFFFF", "FFFFFFFFFF"}} | -- | -- | Get, Set | dedicated timepoint for connection or disconnection
| M-Bus Disconnector script table | M-M | M-M |  | 9 | 0 |  | 0-1:10.0.106.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00010A006AFF" | -- | -- | Get
2 | scripts |  |  | array[16](script9) |  |  | 0x08 | { {1,{{1,70, 0-1:24.4.0.255,3,2}}}, {2,{{1,70, 0-1:24.4.0.255,3,1}}}, {3,{{1,70, 0-2:24.4.0.255,3,2}}}, {4,{{1,70, 0-2:24.4.0.255,3,1}}}, {5,{{1,70, 0-3:24.4.0.255,3,2}}}, {6,{{1,70, 0-3:24.4.0.255,3,1}}}, {7,{{1,70, 0-4:24.4.0.255,3,2}}}, {8,{{1,70, 0-4:24.4.0.255,3,1}}}, {9,{{2,70, 0-1:24.4.0.255,1,0}}}, {10,{{2,70, 0-1:24.4.0.255,2,0}}}, {11,{{2,70, 0-2:24.4.0.255,1,0}}}, {12,{{2,70, 0-2:24.4.0.255,2,0}}}, {13,{{2,70, 0-3:24.4.0.255,1,0}}}, {14,{{2,70, 0-3:24.4.0.255,2,0}}}, {15,{{2,70, 0-4:24.4.0.255,1,0}}}, {16,{{2,70, 0-4:24.4.0.255,2,0}}} } | -- | -- | Get | local and remote connect and disconnect methods of the M-Bus disconnector objects, see E disconnector script table for further details
1 | execute |  |  | long_unsigned |  |  | 0x20 |  | -- | -- | -- | Executes the script specified in parameter data. If data matches one of the script_identifiers in the script table, then the corresponding action_specification is executed. No direct method call possible via remote communication
| Event Objects - M-Bus Master Control logs 1 | M-M | M-M |  | 1 | 0 |  | 0-1:96.11.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001600B04FF" | -- | -- | Get
2 | value |  |  | choice(enum, long_unsigned) |  |  | 0x08 |  | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| Event Objects - M-Bus Master Control logs 2 | M-M | M-M |  | 1 | 0 |  | 0-2:96.11.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002600B04FF" | -- | -- | Get
2 | value |  |  | choice(enum, long_unsigned) |  |  | 0x08 |  | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| Event Objects - M-Bus Master Control logs 3 | M-M | M-M |  | 1 | 0 |  | 0-3:96.11.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003600B04FF" | -- | -- | Get
2 | value |  |  | choice(enum, long_unsigned) |  |  | 0x08 |  | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| Event Objects - M-Bus Master Control logs 4 | M-M | M-M |  | 1 | 0 |  | 0-4:96.11.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004600B04FF" | -- | -- | Get
2 | value |  |  | choice(enum, long_unsigned) |  |  | 0x08 |  | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| M-Bus Master Control log object 1 | M-M | M-M |  | 7 | 1 |  | 0-1:24.5.0.255 |  |  |  | Changes of the states related to the disconnect control are recorded (open, close)
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001180500FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1, 0-1:96.11.4.255, 2, 0}} | -- | -- | Get, (Set) | clock;control event code
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [10..*] | -- | -- | Get
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
| M-Bus Master Control log object 2 | M-M | M-M |  | 7 | 1 |  | 0-2:24.5.0.255 |  |  |  | Changes of the states related to the disconnect control are recorded (open, close)
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002180500FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1, 0-2:96.11.4.255, 2, 0}} | -- | -- | Get, (Set) | clock;control event code
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [10..*] | -- | -- | Get
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
| M-Bus Master Control log object 3 | M-M | M-M |  | 7 | 1 |  | 0-3:24.5.0.255 |  |  |  | Changes of the states related to the disconnect control are recorded (open, close)
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003180500FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1, 0-3:96.11.4.255, 2, 0}} | -- | -- | Get, (Set) | clock;control event code
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [10..*] | -- | -- | Get
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
| M-Bus Master Control log object 4 | M-M | M-M |  | 7 | 1 |  | 0-4:24.5.0.255 |  |  |  | Changes of the states related to the disconnect control are recorded (open, close)
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004180500FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1, 0-4:96.11.4.255, 2, 0}} | -- | -- | Get, (Set) | clock;control event code
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [10..*] | -- | -- | Get
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
| Event Object - M-Bus Event Log | M-M | M-M |  | 1 | 0 |  | 0-0:96.11.3.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000600B03FF" | -- | -- | Get
2 | value |  |  | choice(enum, long_unsigned) |  |  | 0x08 |  | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| M-Bus Event Log | M-M | M-M |  | 7 | 1 |  | 0-0:99.98.3.255 |  |  |  | Event log containing errors and alarms related to all M-Bus devices
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000636203FF" | -- | -- | Get
2 | buffer |  |  | array |  |  | 0x08 |  | -- | -- | Get | selective access per range
3 | capture_objects |  |  | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1, 0-0:96.11.3.255, 2, 0}} | -- | -- | Get, (Set) | clock;event code
4 | capture_period |  |  | double_long_unsigned |  |  | 0x18 | 0 | -- | -- | Get | asynchronously
5 | sort_method |  |  | enum |  |  | 0x20 | 1 | -- | -- | Get | unsorted (FIFO)
6 | sort_object |  |  | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | unsorted
7 | entries_in_use |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | profile_entries |  |  | double_long_unsigned |  |  | 0x38 | [10..*] | -- | -- | Get
1 | reset | [5 empty] | 0x58 |  | -- | -- | Action
Local communication - IEC/HDLC Optical port
| IEC local port setup - IEC Optical port | O | O |  | 19 | 1 |  | 0-0:20.0.0.255 |  |  |  | Used in case IEC1107 is supported on the Optical port s well
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000140000FF" | -- | -- | Get
2 | default_mode |  |  | enum |  |  | 0x08 |  | -- | Set | Get, Set
3 | default_baud |  |  | enum |  |  | 0x10 |  | -- | Set | Get, Set
4 | prop_baud |  |  | enum |  |  | 0x18 |  | -- | Set | Get, Set
5 | response_time |  |  | enum |  |  | 0x20 |  | -- | Set | Get, Set
6 | device_addr |  |  | octet_string |  |  | 0x28 |  | -- | Set | Get, Set
7 | pass_p1 |  |  | octet_string |  |  | 0x30 |  | -- | Set | Set
8 | pass_p2 |  |  | octet_string |  |  | 0x38 |  | -- | Set | Set
9 | pass_p3 |  |  | octet_string |  |  | 0x40 |  | -- | Set | Set
| IEC HDLC setup - HDLC Optical port | M | M |  | 23 | 1 |  | 0-0:22.0.0.255 |  |  |  | Mandatory HDLC on Optical port.
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000160000FF" | -- | -- | Get
2 | comm_speed |  |  | enum |  |  | 0x08 | 5 | -- | Set | Get, Set
3 | window_size_transmit |  |  | unsigned |  |  | 0x10 | 1 | -- | Set | Get, Set
4 | window_size_receive |  |  | unsigned |  |  | 0x18 | 1 | -- | Set | Get, Set
5 | max_info_field_lenght_transmit |  |  | long_unsigned |  |  | 0x20 | [32..2030] | -- | Set | Get, Set
6 | max_info_field_lenght_receive |  |  | long_unsigned |  |  | 0x28 | [32..2030] | -- | Set | Get, Set
7 | inter_octet_time_out |  |  | long_unsigned |  |  | 0x30 | [20..6000] | -- | Set | Get, Set
8 | inactivity_time_out |  |  | long_unsigned |  |  | 0x38 |  | -- | Set | Get, Set
9 | device_address |  |  | long_unsigned |  |  | 0x40 |  | -- | -- | Get, Set
Abstract objects - TCP/IP profile setup
| TCP-UDP setup | M | M |  | 41 | 0 |  | 0-0:25.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000190000FF" | -- | -- | Get
2 | TCP-UDP_port |  |  | long_unsigned |  |  | 0x08 | choice(4059, 61616) | -- | -- | Get, Set
3 | IP_reference |  |  | octet_string[6] |  |  | 0x10 | Choice(0-0:25.1.0.255,0-0:25.7.0.255) | -- | -- | Get
4 | MSS |  |  | long_unsigned |  |  | 0x18 | 1280 | -- | -- | Get, Set
5 | nb_of_sim_conn |  |  | unsigned |  |  | 0x20 | 1 | -- | -- | Get, Set
6 | inactivity_time_out |  |  | long_unsigned |  |  | 0x28 | 180 | -- | -- | Get, Set
| IPv4 setup | M-I4 | M-I4 |  | 42 | 0 |  | 0-0:25.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000190100FF" | -- | -- | Get
2 | DL_reference |  |  | octet_string[6] |  |  | 0x08 | Choice(0-0:25.3.0.255, 0-0:25.2.0.255) | -- | -- | Get, Set
3 | IP_address |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get, Set
4 | multicast_IP_address |  |  | array[0..*] |  |  | 0x18 |  | -- | -- | Get, Set
5 | IP_options |  |  | array[0..*] |  |  | 0x20 |  | -- | -- | Get, Set
6 | subnet_mask |  |  | double_long_unsigned |  |  | 0x28 |  | -- | -- | Get, Set
7 | gateway_IP_address |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get, Set
8 | use_DHCP_flag |  |  | boolean |  |  | 0x38 |  | -- | -- | Get, Set
9 | primary_DNS_address |  |  | double_long_unsigned |  |  | 0x40 |  | -- | -- | Get, Set
10 | secondary_DNS_address |  |  | double_long_unsigned |  |  | 0x48 |  | -- | -- | Get, Set
1 | add_mc_IP_address |  |  | double_long_unsigned |  |  | 0x60 |  | -- | -- | --
2 | delete_mc_IP_address |  |  | double_long_unsigned |  |  | 0x68 |  | -- | -- | --
3 | get_nbof_mc_IP_addresses |  |  | unsigned |  |  | 0x70 |  | -- | -- | --
| IPv6 setup | M-I6 | M-I6 |  | 48 | 0 |  | 0-0:25.7.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000190700FF" | -- | -- | Get
2 | DL_reference |  |  | octet_string[6] |  |  | 0x08 | Choice(0-0:25.3.0.255, 0-0:25.2.0.255) | -- | -- | Get, Set
3 | address_config_mode |  |  | enum |  |  | 0x10 | 0 | -- | -- | Get, Set
4 | unicast_IPv6_addresses |  |  | array[0..*](IPv6_address) |  |  | 0x18 |  | -- | -- | Get, Set
5 | multicast_IPv6_addresses |  |  | array[0..*](IPv6_address) |  |  | 0x20 |  | -- | -- | Get, Set
6 | gateway_IPv6_address |  |  | array[0..*](IPv6_address) |  |  | 0x28 |  | -- | -- | Get, Set
7 | primary_DNS_address |  |  | IPv6_address |  |  | 0x30 |  | -- | -- | Get, Set
8 | secondary_DNS_address |  |  | IPv6_address |  |  | 0x38 |  | -- | -- | Get, Set
9 | traffic_class |  |  | unsigned |  |  | 0x40 |  | -- | -- | Get, Set
10 | neighbor_discovery_setup |  |  | array[0..*](neighbour_discovery_setup_element) |  |  | 0x48 |  | -- | -- | Get, Set
1 | add_IPv6_address |  |  | IPv6_address_entry |  |  | 0x60 |  | -- | -- | (Action)
2 | remove_IPv6_address |  |  | IPv6_address_entry |  |  | 0x68 |  | -- | -- | (Action)
| PPP setup | M-G | M-G |  | 44 | 0 |  | 0-0:25.3.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000190300FF" | -- | -- | Get
2 | PHY_refernce |  |  | octet_string[6] |  |  | 0x08 | 0-0:25.4.0.255 | -- | -- | Get, Set
3 | LCP_options |  |  | array[1..8](LCP_options_element) |  |  | 0x10 | { {3, 4, 0xC023},... } | -- | -- | Get, Set | { LCP-option-type := Auth-Prot, LCP-Option-Length := 2, LCP-option-data := PAP}
4 | IPCP_options |  |  | array[1..5](IPCP_options_element) |  |  | 0x18 | { {2, 4, 0x0000},... } | -- | -- | Get, Set | { IPCP-option-type := IP-comp-prot, IPCP-option-Length := 2, IPCP-option-data := No-IP-Compresion-is-used}
5 | PPP_authentication |  |  | PPP_authentication_type |  |  | 0x20 |  | -- | -- | Get, Set | { choice( NULL, { user-name, PAP-password} ) }
Abstract objects - Push setup
| Push setup - Interval_1 | M | M |  | 40 | 0 |  | 0-1:25.9.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0001190900FF" | -- | -- | Get
2 | push_object_list |  |  | array[0..*](capture_object_definition) |  |  | 0x08 |  | -- | -- | Get, Set
3 | send_destination_and_method |  |  | send_destination_and_method_type |  |  | 0x10 | {[0..4],*,0} | -- | -- | Get, Set
4 | communication_window |  |  | array[0..*](window_element) |  |  | 0x18 |  | -- | -- | Get, Set
5 | randomisation_start_interval |  |  | long_unsigned |  |  | 0x20 | 0 | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
6 | number_of_retries |  |  | unsigned |  |  | 0x28 |  | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
7 | repetition_delay |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get, Set | Delay in seconds between repetitions
1 | push |  |  | integer |  |  | 0x38 |  | -- | Action | Action
| Push setup - Interval_2 | M | M |  | 40 | 0 |  | 0-2:25.9.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0002190900FF" | -- | -- | Get
2 | push_object_list |  |  | array[0..*](capture_object_definition) |  |  | 0x08 |  | -- | -- | Get, Set
3 | send_destination_and_method |  |  | send_destination_and_method_type |  |  | 0x10 | {[0..4],*,0} | -- | -- | Get, Set
4 | communication_window |  |  | array[0..*](window_element) |  |  | 0x18 |  | -- | -- | Get, Set
5 | randomisation_start_interval |  |  | long_unsigned |  |  | 0x20 | 0 | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
6 | number_of_retries |  |  | unsigned |  |  | 0x28 |  | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
7 | repetition_delay |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get, Set | Delay in seconds between repetitions
1 | push |  |  | integer |  |  | 0x38 |  | -- | Action | Action
| Push setup - Interval_3 | M | M |  | 40 | 0 |  | 0-3:25.9.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0003190900FF" | -- | -- | Get
2 | push_object_list |  |  | array[0..*](capture_object_definition) |  |  | 0x08 |  | -- | -- | Get, Set
3 | send_destination_and_method |  |  | send_destination_and_method_type |  |  | 0x10 | {[0..4],*,0} | -- | -- | Get, Set
4 | communication_window |  |  | array[0..*](window_element) |  |  | 0x18 |  | -- | -- | Get, Set
5 | randomisation_start_interval |  |  | long_unsigned |  |  | 0x20 | 0 | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
6 | number_of_retries |  |  | unsigned |  |  | 0x28 |  | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
7 | repetition_delay |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get, Set | Delay in seconds between repetitions
1 | push |  |  | integer |  |  | 0x38 |  | -- | Action | Action
| Push setup - On Alarm | M | M |  | 40 | 0 |  | 0-4:25.9.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0004190900FF" | -- | -- | Get
2 | push_object_list |  |  | array[0..*](capture_object_definition) |  |  | 0x08 |  | -- | -- | Get, Set
3 | send_destination_and_method |  |  | send_destination_and_method_type |  |  | 0x10 | {[0..4],*,0} | -- | -- | Get, Set
4 | communication_window |  |  | array[0..*](window_element) |  |  | 0x18 |  | -- | -- | Get, Set
5 | randomisation_start_interval |  |  | long_unsigned |  |  | 0x20 | 0 | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
6 | number_of_retries |  |  | unsigned |  |  | 0x28 |  | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
7 | repetition_delay |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get, Set | Delay in seconds between repetitions
1 | push |  |  | integer |  |  | 0x38 |  | -- | Action | Action
| Push setup - On Connectivity | M | M |  | 40 | 0 |  | 0-0:25.9.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000190900FF" | -- | -- | Get
2 | push_object_list |  |  | array[0..*](capture_object_definition) |  |  | 0x08 |  | -- | -- | Get, Set
3 | send_destination_and_method |  |  | send_destination_and_method_type |  |  | 0x10 | {[0..4],*,0} | -- | -- | Get, Set
4 | communication_window |  |  | array[0..*](window_element) |  |  | 0x18 |  | -- | -- | Get, Set
5 | randomisation_start_interval |  |  | long_unsigned |  |  | 0x20 | 0 | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
6 | number_of_retries |  |  | unsigned |  |  | 0x28 |  | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
7 | repetition_delay |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get, Set | Delay in seconds between repetitions
1 | push |  |  | integer |  |  | 0x38 |  | -- | Action | Action
| Push setup - On Installation | M | M |  | 40 | 0 |  | 0-7:25.9.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0007190900FF" | -- | -- | Get
2 | push_object_list |  |  | array[0..*](capture_object_definition) |  |  | 0x08 |  | -- | -- | Get, Set
3 | send_destination_and_method |  |  | send_destination_and_method_type |  |  | 0x10 | {[0..4],*,0} | -- | -- | Get, Set
4 | communication_window |  |  | array[0..*](window_element) |  |  | 0x18 |  | -- | -- | Get, Set
5 | randomisation_start_interval |  |  | long_unsigned |  |  | 0x20 | 0 | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
6 | number_of_retries |  |  | unsigned |  |  | 0x28 |  | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
7 | repetition_delay |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get, Set | Delay in seconds between repetitions
1 | push |  |  | integer |  |  | 0x38 |  | -- | Action | Action
| Push setup - On Power down | O | O |  | 40 | 0 |  | 0-5:25.9.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0005190900FF" | -- | -- | Get
2 | push_object_list |  |  | array[0..*](capture_object_definition) |  |  | 0x08 |  | -- | -- | Get, Set
3 | send_destination_and_method |  |  | send_destination_and_method_type |  |  | 0x10 | {[0..4],*,0} | -- | -- | Get, Set
4 | communication_window |  |  | array[0..*](window_element) |  |  | 0x18 |  | -- | -- | Get, Set
5 | randomisation_start_interval |  |  | long_unsigned |  |  | 0x20 | 0 | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
6 | number_of_retries |  |  | unsigned |  |  | 0x28 |  | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
7 | repetition_delay |  |  | long_unsigned |  |  | 0x30 |  | -- | -- | Get, Set | Delay in seconds between repetitions
1 | push |  |  | integer |  |  | 0x38 |  | -- | Action | Action
| Push script table | M | M |  | 9 | 0 |  | 0-0:10.0.108.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00000A006CFF" | -- | -- | Get
2 | scripts |  |  | array[6..*](script9) |  |  | 0x08 | choice( { {1,{{2,40,0-1:25.9.0.255,1,0}}}, //Push - Interval_1 {2,{{2,40,0-2:25.9.0.255,1,0}}}, //Push - Interval_2 {3,{{2,40,0-3:25.9.0.255,1,0}}}, //Push - Interval_3 {4,{{2,40,0-4:25.9.0.255,1,0}}}, //Push - On Alarm {5,{{2,40,0-0:25.9.0.255,1,0}}}, //Push - On Connectivity {6,{{2,40,0-7:25.9.0.255,1,0}}}, //Push - On Installation ... }, { {1,{{2,40,0-1:25.9.0.255,1,0}}}, //Push - Interval_1 {2,{{2,40,0-2:25.9.0.255,1,0}}}, //Push - Interval_2 {3,{{2,40,0-3:25.9.0.255,1,0}}}, //Push - Interval_3 {4,{{2,40,0-4:25.9.0.255,1,0}}}, //Push - On Alarm {5,{{2,40,0-0:25.9.0.255,1,0}}}, //Push - On Connectivity {6,{{2,40,0-7:25.9.0.255,1,0}}}, //Push - On Installation {8,{{2,40,0-6:25.9.0.255,1,0}}}, //Push - Consumer Information ... }, { {1,{{2,40,0-1:25.9.0.255,1,0}}}, //Push - Interval_1 {2,{{2,40,0-2:25.9.0.255,1,0}}}, //Push - Interval_2 {3,{{2,40,0-3:25.9.0.255,1,0}}}, //Push - Interval_3 {4,{{2,40,0-4:25.9.0.255,1,0}}}, //Push - On Alarm {5,{{2,40,0-0:25.9.0.255,1,0}}}, //Push - On Connectivity {6,{{2,40,0-7:25.9.0.255,1,0}}}, //Push - On Installation {7,{{2,40,0-5:25.9.0.255,1,0}}}, //Push - On Power Down ... }, { {1,{{2,40,0-1:25.9.0.255,1,0}}}, //Push - Interval_1 {2,{{2,40,0-2:25.9.0.255,1,0}}}, //Push - Interval_2 {3,{{2,40,0-3:25.9.0.255,1,0}}}, //Push - Interval_3 {4,{{2,40,0-4:25.9.0.255,1,0}}}, //Push - On Alarm {5,{{2,40,0-0:25.9.0.255,1,0}}}, //Push - On Connectivity {6,{{2,40,0-7:25.9.0.255,1,0}}}, //Push - On Installation {7,{{2,40,0-5:25.9.0.255,1,0}}}, //Push - On Power down {8,{{2,40,0-6:25.9.0.255,1,0}}}, //Push - Consumer Information ... }) | -- | -- | Get, (Set) | The first 6 scripts are mandatory, script 7 and 8 only need to be present if the optional elements (push setup on power down and CIP) are present as well. Please note that the assignment of the script_identifier is fixed.
1 | execute |  |  | long_unsigned |  |  | 0x20 |  | -- | -- | Action
| Push action scheduler - Interval_1 | M | M |  | 22 | 0 |  | 0-1:15.0.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00010F0004FF" | -- | -- | Get
2 | executed_script |  |  | script22 |  |  | 0x08 | {0-0:10.0.108.255,1} | -- | -- | Get, (Set)
3 | type |  |  | enum |  |  | 0x10 | 5 | -- | -- | Get, (Set)
4 | execution_time |  |  | array[0..*](execution_time_date) |  |  | 0x18 |  | -- | -- | Get, Set
| Push action scheduler - Interval_2 | M | M |  | 22 | 0 |  | 0-2:15.0.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00020F0004FF" | -- | -- | Get
2 | executed_script |  |  | script22 |  |  | 0x08 | {0-0:10.0.108.255,2} | -- | -- | Get, (Set)
3 | type |  |  | enum |  |  | 0x10 | 5 | -- | -- | Get, (Set)
4 | execution_time |  |  | array[0..*](execution_time_date) |  |  | 0x18 |  | -- | -- | Get, Set
| Push action scheduler - Interval_3 | M | M |  | 22 | 0 |  | 0-3:15.0.4.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00030F0004FF" | -- | -- | Get
2 | executed_script |  |  | script22 |  |  | 0x08 | {0-0:10.0.108.255,3} | -- | -- | Get, (Set)
3 | type |  |  | enum |  |  | 0x10 | 5 | -- | -- | Get, (Set)
4 | execution_time |  |  | array[0..*](execution_time_date) |  |  | 0x18 |  | -- | -- | Get, Set
Remote communication - Abstract Objects for Network Mgmt
| Auto connect | M | M |  | 29 | 2 |  | 0-0:2.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000020100FF" | -- | -- | Get
2 | mode |  |  | enum |  |  | 0x08 | 101 | -- | -- | Get, Set
3 | repetitions |  |  | unsigned |  |  | 0x10 | 0 | -- | -- | Get, Set
4 | repetition_delay |  |  | long_unsigned |  |  | 0x18 | 0 | -- | -- | Get, Set
5 | calling_window |  |  | array[0..*](window_element) |  |  | 0x20 |  | -- | -- | Get, Set
6 | destination_list |  |  | array[0..*] |  |  | 0x28 |  | -- | -- | Get, (Set)
1 | connect |  |  | integer |  |  | 0x30 |  | -- | -- | Action
| MAC address setup | M-E¦M-G3 | M-E¦M-G3 |  | 43 | 0 |  | 0-0:25.2.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000190200FF" | -- | -- | Get
2 | MAC_address |  |  | octet_string |  |  | 0x08 |  | -- | -- | Get
Remote communication - GSM/GPRS Setup Objects
| GPRS modem setup | M-G | M-G |  | 45 | 0 |  | 0-0:25.4.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000190400FF" | -- | -- | Get
2 | APN |  |  | octet_string[0..64] |  |  | 0x08 |  | -- | -- | Get, Set | An APN with a size of 64 bytes at least is supported, i.e. [0.64] is mandatoty but can be longer
3 | PIN_code |  |  | long_unsigned |  |  | 0x10 |  | -- | -- | Get, Set
4 | quality_of_service |  |  | quality_of_service_type |  |  | 0x18 |  | -- | -- | Get, Set
| Modem configuration | M-G | M-G |  | 27 | 1 |  | 0-0:2.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000020000FF" | -- | -- | Get
2 | comm_speed |  |  | enum |  |  | 0x08 |  | -- | -- | Get, Set
3 | initialization_string |  |  | array |  |  | 0x10 |  | -- | -- | Get, Set
4 | modem_profile |  |  | array |  |  | 0x18 |  | -- | -- | Get, Set
| Auto answer | M-G | M-G |  | 28 | 2 |  | 0-0:2.2.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "0000020200FF" | -- | -- | Get
2 | mode |  |  | enum |  |  | 0x08 |  | -- | -- | Get, Set
3 | listening_window |  |  | array[0..*] |  |  | 0x10 |  | -- | -- | Get, Set | Array[0] equals always listening
4 | status |  |  | enum |  |  | 0x18 |  | -- | -- | Get, Set
5 | number_of_calls |  |  | unsigned |  |  | 0x20 |  | -- | -- | Get, Set
6 | number_of_rings |  |  | nr_rings_type |  |  | 0x28 |  | -- | -- | Get, Set
7 | list_of_allowed_callers |  |  | array[0..*](list_of_allowed_callers_element) |  |  | 0x30 |  | -- | -- | Get, Set | phone number is an ASCII coded octet-string of phone number length
Remote communication - G3-PLC Setup Objects
| G3-PLC MAC layer counters | M-G3 | M-G3 |  | 90 | 1 |  | 0-0:29.0.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00001D0000FF" | -- | -- | Get
2 | mac_Tx_data_packet_count |  |  | double_long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | mac_Rx_data_packet_count |  |  | double_long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | mac_Tx_cmd_packet_count |  |  | double_long_unsigned |  |  | 0x18 |  | -- | -- | Get
5 | mac_Rx_cmd_packet_count |  |  | double_long_unsigned |  |  | 0x20 |  | -- | -- | Get
6 | mac_CSMA_fail_count |  |  | double_long_unsigned |  |  | 0x28 |  | -- | -- | Get
7 | mac_CSMA_no_ACK_count |  |  | double_long_unsigned |  |  | 0x30 |  | -- | -- | Get
8 | mac_bad_CRC_count |  |  | double_long_unsigned |  |  | 0x38 |  | -- | -- | Get
9 | mac_Tx_data_broadcast_count |  |  | double_long_unsigned |  |  | 0x40 |  | -- | -- | Get
10 | mac_Rx_data_broadcast_count |  |  | double_long_unsigned |  |  | 0x48 |  | -- | -- | Get
1 | reset |  |  | integer |  |  | 0x50 |  | -- | -- | Action
| G3-PLC MAC setup | M-G3 | M-G3 |  | 91 | 1 |  | 0-0:29.1.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00001D0100FF" | -- | -- | Get
2 | mac_short_address |  |  | long_unsigned |  |  | 0x08 |  | -- | -- | Get
3 | mac_RC_coord |  |  | long_unsigned |  |  | 0x10 |  | -- | -- | Get
4 | mac_PAN_id |  |  | long_unsigned |  |  | 0x18 |  | -- | -- | Get
5 | mac_key_table |  |  | array |  |  | 0x20 |  | -- | -- | Set
6 | mac_frame_counter |  |  | double_long_unsigned |  |  | 0x28 |  | -- | -- | Get
7 | mac_tone_mask |  |  | bit_string |  |  | 0x30 | "\000000000000000000000000000000000000111111111111111111111111111111111111" | -- | -- | Get, Set
8 | mac_TMR_TTL |  |  | unsigned |  |  | 0x38 | 2 | -- | Set | Get, Set
9 | mac_max_frame_retries |  |  | unsigned |  |  | 0x40 | 5 | -- | Set | Get, Set
10 | mac_neighbour_table_entry_TTL |  |  | unsigned |  |  | 0x48 | 255 | -- | Set | Get, Set
11 | mac_neighbour_table |  |  | array |  |  | 0x50 |  | -- | -- | Get
12 | mac_high_priority_window_size |  |  | unsigned |  |  | 0x58 | 7 | -- | Set | Get, Set
13 | mac_CSMA_fairness_limit |  |  | unsigned |  |  | 0x60 | 25 | -- | Set | Get, Set
14 | mac_beacon_randomization_window_length |  |  | unsigned |  |  | 0x68 | 12 | -- | Set | Get, Set
15 | mac_A |  |  | unsigned |  |  | 0x70 | 8 | -- | Set | Get, Set
16 | mac_K |  |  | unsigned |  |  | 0x78 | 5 | -- | Set | Get, Set
17 | mac_min_CW_attempts |  |  | unsigned |  |  | 0x80 | 10 | -- | Set | Get, Set
18 | mac_cenelec_legacy_mode |  |  | unsigned |  |  | 0x88 | 1 | -- | -- | Get
19 | mac_FCC_legacy_mode |  |  | unsigned |  |  | 0x90 | 1 | -- | -- | Get
20 | mac_max_BE |  |  | unsigned |  |  | 0x98 | 8 | -- | Set | Get, Set
21 | mac_max_CSMA_backoffs |  |  | unsigned |  |  | 0xA0 | 50 | -- | Set | Get, Set
22 | mac_min_BE |  |  | unsigned |  |  | 0xA8 | 3 | -- | Set | Get, Set
1 | mac_get_neighbour_table_entry |  |  | long_unsigned |  |  | 0xB0 |  | -- | -- | Action
| G3-PLC MAC 6LoWPAN adaptation layer setup | M-G3 | M-G3 |  | 92 | 1 |  | 0-0:29.2.0.255
1 | logical_name |  |  | octet_string[6] |  |  |  | "00001D0200FF" | -- | -- | Get
2 | adp_max_hops |  |  | unsigned |  |  | 0x08 |  | -- | -- | Get, Set
3 | adp_weak_LQI_value |  |  | unsigned |  |  | 0x10 |  | -- | -- | Get, Set
4 | adp_security_level |  |  | unsigned |  |  | 0x18 | 5 | -- | -- | Get, Set | keys must be defined: Shall we define defaults or add it to CTI file ?
5 | adp_prefix_table |  |  | array |  |  | 0x20 |  | -- | -- | Get
6 | adp_routing_configuration |  |  | array |  |  | 0x28 |  | -- | -- | Get, Set
7 | adp_broadcast_log_table_entry_TTL |  |  | long_unsigned |  |  | 0x30 | 2 | -- | -- | Get, Set
8 | adp_routing_table |  |  | array |  |  | 0x38 |  | -- | -- | Get
9 | adp_context_information_table |  |  | array |  |  | 0x40 |  | -- | -- | Get
10 | adp_blacklist_table |  |  | array |  |  | 0x48 |  | -- | -- | Get
11 | adp_broadcast_log_table |  |  | array |  |  | 0x50 |  | -- | -- | Get
12 | adp_group_table |  |  | array |  |  | 0x58 |  | -- | -- | Get
13 | adp_max_join_wait_time |  |  | long_unsigned |  |  | 0x60 | 20 | -- | -- | Get, Set
14 | adp_path_discovery_time |  |  | unsigned |  |  | 0x68 | 40 | -- | -- | Get, Set
15 | adp_active_key_index |  |  | unsigned |  |  | 0x70 |  | -- | -- | Get
16 | adp_metric_type |  |  | unsigned |  |  | 0x78 | 0x0F | -- | -- | Get, Set
17 | adp_coord_short_address |  |  | long_unsigned |  |  | 0x80 | 0x0000 | -- | -- | Get, Set
18 | adp_disable_default_routing |  |  | boolean |  |  | 0x88 | 0 | -- | -- | Get, Set
19 | adp_device_type |  |  | enum |  |  | 0x90 | 0 | -- | -- | Get, Set
Note on C1: M=mandatory, O=optional, NA=not applicable; M-x=mandatory for extension x
Note on B786: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B799: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B812: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B825: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B838: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B851: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B1380: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B1411: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B1442: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B1509: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!

## Events
3.3 Event definitions and assignments
Number | Hex | Name | Description | Standard Event Log | Fraud Detection Log | Disconnector Control Log | M-Bus Event Log | M-Bus Control Log 1 | M-Bus Control Log 2 | M-Bus Control Log 3 | M-Bus Control Log 4 | Power Quality Event Log | Communication Log | Mandatory/optionl
1 | 01 | Power Down | Indicates a complete power down of the device. Please note that this is related to the device and not necessarily to the network. | x | [9 empty] | M
2 | 02 | Power Up | Indicates that the device is powered again after a complete power down. | x | [9 empty] | M
3 | 03 | Daylight saving time enabled or disabled | Indicates the regular change from and to daylight saving time. The time stamp shows the time before the change. This event is not set in case of manual clock changes and in case of power failures. | x | [9 empty] | M
4 | 04 | Clock adjusted (old date/time) | Indicates that the clock has been adjusted. The date/time that is stored in the event log is the old date/time before adjusting the clock. | x | [9 empty] | M
5 | 05 | Clock adjusted (new date/time) | Indicates that the clock has been adjusted. The date/time that is stored in the event log is the new date/time after adjusting the clock. | x | [9 empty] | M
6 | 06 | Clock invalid | Indicates that clock may be invalid, i.e. if the power reserve of the clock has exhausted. It is set at power up. | x | [9 empty] | M
7 | 07 | Replace Battery | Indicates that the battery must be exchanged due to the expected end of life time. | x | [9 empty] | O
8 | 08 | Battery voltage low | Indicates that the current battery voltage is low. | x | [9 empty] | O
9 | 09 | TOU activated | Indicates that the passive TOU has been activated. | x | [9 empty] | M
10 | 0A | Error register cleared | Indicates that the error register was cleared. | x | [9 empty] | M
11 | 0B | Alarm register cleared | Indicates that the alarm register was cleared. | x | [9 empty] | M
12 | 0C | Program memory error | Indicates a physical or a logical error in the program memory. | x | [9 empty] | M
13 | 0D | RAM error | Indicates a physical or a logical error in the RAM. | x | [9 empty] | M
14 | 0E | NV memory error | Indicates a physical or a logical error in the non volatile memory | x | [9 empty] | M
15 | 0F | Watchdog error | Indicates a watch dog reset or a hardware reset of the microcontroller. | x | [9 empty] | M
16 | 10 | Measurement system error | Indicates a logical or physical error in the measurement system | x | [9 empty] | M
17 | 11 | Firmware ready for activation | Indicates that the new firmware has been successfully downloaded and verified, i.e. it is ready for activation | x | [9 empty] | M
18 | 12 | Firmware activated | Indicates that a new firmware has been activated | x | [9 empty] | M
19 | 13 | Passive TOU programmed | The passive structures of TOU or a new activation date/time were programed | x | [9 empty] | O
20 | 14 | External alert detected | Indicates a signal detected on the meter's input terminal | x | [9 empty] | O
21 | 15 | reserved for future use
22 | 16 | reserved for future use
23 | 17 | reserved for future use
24 | 18 | reserved for future use
25 | 19 | reserved for future use
26 | 1A | reserved for future use
27 | 1B | reserved for future use
28 | 1C | reserved for future use
29 | 1D | reserved for future use
30 | 1E | reserved for future use
31 | 1F | reserved for future use
32 | 20 | reserved for future use
33 | 21 | reserved for future use
34 | 22 | reserved for future use
35 | 23 | reserved for future use
36 | 24 | reserved for future use
37 | 25 | reserved for future use
38 | 26 | reserved for future use
39 | 27 | reserved for future use
40 | 28 | Terminal cover removed | Indicates that the terminal cover has been removed. |  | x | [8 empty] | O
41 | 29 | Terminal cover closed | Indicates that the terminal cover has been closed. |  | x | [8 empty] | O
42 | 2A | Strong DC field detected | Indicates that a strong magnetic DC field has been detected. |  | x | [8 empty] | O
43 | 2B | No strong DC field anymore | Indicates that the strong magnetic DC field has disappeared. |  | x | [8 empty] | O
44 | 2C | Meter cover removed | Indicates that the meter cover has been removed. |  | x | [8 empty] | O
45 | 2D | Meter cover closed | Indicates that the meter cover has been closed. |  | x | [8 empty] | O
46 | 2E | Association authentication failure (n time failed authentication) | Indicates that a user tried to gain LLS access with wrong password (intrusion detection) or HLS access challenge processing failed n-times |  | x | [8 empty] | M
47 | 2F | One or more parameters changed | Indicates the change of at least one parameter | x | [9 empty] | M
48 | 30 | Global key(s) changed | One or more global keys changed | x | [9 empty] | M
49 | 31 | Decryption or authentication failure (n time failure) | Decryption with currently valid key (global or dedicated) failed to generate a valid APDU or authentication tag |  | x | [8 empty] | M
50 | 32 | Replay attack | Receive frame counter value less or equal to the last successfully received frame counter in the received APDU Event signalizes as well the situation when the DC has lost the frame counter synchronization. |  | x | [8 empty] | M
51 | 33 | FW verification failed | Indicates the transferred firmware verification failed i.e. cannot be activated. | x | [9 empty] | M
52 | 34 | Unexpected consumption | Indicates consumption is detected at least on one phase when the disconnector has been disconnected | x | [9 empty] | O
53 | 35 | reserved for future use
54 | 36 | reserved for future use
55 | 37 | reserved for future use
56 | 38 | reserved for future use
57 | 39 | reserved for future use
58 | 3A | reserved for future use
59 | 3B | Disconnector ready for manual reconnection | Indicates that the disconnector has been set into the Ready_for_reconnection state and can be manually reconnected |  |  | x | [7 empty] | M-D
60 | 3C | Manual disconnection | Indicates that the disconnector has been manually disconnected. |  |  | x | [7 empty] | M-D
61 | 3D | Manual connection | Indicates that the disconnector has been manually connected. |  |  | x | [7 empty] | M-D
62 | 3E | Remote disconnection | Indicates that the disconnector has been remotely disconnected. |  |  | x | [7 empty] | M-D
63 | 3F | Remote connection | Indicates that the disconnector has been remotely connected. |  |  | x | [7 empty] | M-D
64 | 40 | Local disconnection | Indicates that the disconnector has been locally disconnected (i.e. via the limiter or current supervision monitors). |  |  | x | [7 empty] | M-D
65 | 41 | Limiter threshold exceeded | Indicates that the limiter threshold has been exceeded. |  |  | x | [7 empty] | M-D
66 | 42 | Limiter threshold ok | Indicates that the monitored value of the limiter dropped below the threshold. |  |  | x | [7 empty] | M-D
67 | 43 | Limiter threshold changed | Indicates that the limiter threshold has been changed |  |  | x | [7 empty] | M-D
68 | 44 | Disconnect/Reconnect failure | Indicates that the a failure of disconnection or reconnection has happened (control state does not match output state) |  |  | x | [7 empty] | O
69 | 45 | Local reconnection | Indicates that the disconnector has been locally re-connected (i.e. via the limiter or current supervision monitors). |  |  | x | [7 empty] | M-D
70 | 46 | Supervision monitor 1 threshold exceeded | Indicates that the supervision monitor threshold has been exceeded. |  |  | x | [7 empty] | M-L
71 | 47 | Supervision monitor 1 threshold ok | Indicates that the monitored value dropped below the threshold. |  |  | x | [7 empty] | M-L
72 | 48 | Supervision monitor 2 threshold exceeded | Indicates that the supervision monitor threshold has been exceeded. |  |  | x | [7 empty] | M-L
73 | 49 | Supervision monitor 2 threshold ok | Indicates that the monitored value dropped below the threshold. |  |  | x | [7 empty] | M-L
74 | 4A | Supervision monitor 3 threshold exceeded | Indicates that the supervision monitor threshold has been exceeded. |  |  | x | [7 empty] | M-L
75 | 4B | Supervision monitor 3 threshold ok | Indicates that the monitored value dropped below the threshold. |  |  | x | [7 empty] | M-L
76 | 4C | Undervoltage L1 | Indicates undervoltage on at least L1 phase was detected. | [8 empty] | x |  | M
77 | 4D | Undervoltage L2 | Indicates undervoltage on at least L2 phase was detected. | [8 empty] | x |  | M
78 | 4E | Undervoltage L3 | Indicates undervoltage on at least L3 phase was detected. | [8 empty] | x |  | M
79 | 4F | Overvoltage L1 | Indicates overvoltage on at least L1 phase was detected. | [8 empty] | x |  | M
80 | 50 | Overvoltage L2 | Indicates overvoltage on at least L2 phase was detected. | [8 empty] | x |  | M
81 | 51 | Overvoltage L3 | Indicates overvoltage on at least L3 phase was detected. | [8 empty] | x |  | M
82 | 52 | Missing voltage L1 | Indicates that the voltage on at least L1 phase has fallen below the Umin threshold for longer than the time delay. | [8 empty] | x |  | M
83 | 53 | Missing voltage L2 | Indicates that the voltage on at least L2 phase has fallen below the Umin threshold for longer than the time delay. | [8 empty] | x |  | M
84 | 54 | Missing voltage L3 | Indicates that the voltage on at least L3 phase has fallen below the Umin threshold for longer than the time delay. | [8 empty] | x |  | M
85 | 55 | Voltage L1 normal | Indicates that the mains voltage is in normal limits again, e.g. after overvoltage. | [8 empty] | x |  | M
86 | 56 | Voltage L2 normal | Indicates that the mains voltage is in normal limits again, e.g. after overvoltage. | [8 empty] | x |  | M
87 | 57 | Voltage L3 normal | Indicates that the mains voltage is in normal limits again, e.g. after overvoltage. | [8 empty] | x |  | M
88 | 58 | Phase sequence reversal | Indicates wrong mains connection. Usually indicates fraud or wrong installation. For poly phase connection only! | x | [9 empty] | O
89 | 59 | Missing neutral | Indicates that the neutral connection from the supplier to the meter is interrupted (but the neutral connection to the load prevails). The phase voltages measured by the meter may differ from their nominal values | x | [9 empty] | O
90 | 5A | Phase Asymmetry | Indicates phase asymmetry due to large unbalance of loads connected | [8 empty] | x |  | O
91 | 5B | Current Reversal | Indicates unexpected energy export (for devices which are configured for energy import measurement only) |  | x | [8 empty] | O
92 | 5C | Bad Voltage Quality L1 | Indicates that during each period of one week 95 % of the 10 min mean r.m.s, values of the supply voltage are within the range of Un+/- 10 % and all 10 mín mean r.m.s. values of the supply voltage shall be within the range of Un + 10%/- 15%. (acc. EN50160:2010, section 4.2.2) | [8 empty] | x |  | O
93 | 5D | Bad Voltage Quality L2 | Indicates that during each period of one week 95 % of the 10 min mean r.m.s, values of the supply voltage are within the range of Un+/- 10 % and all 10 mín mean r.m.s. values of the supply voltage shall be within the range of Un + 10%/- 15%. (acc. EN50160:2010, section 4.2.2) | [8 empty] | x |  | O
94 | 5E | Bad Voltage Quality L3 | Indicates that during each period of one week 95 % of the 10 min mean r.m.s, values of the supply voltage are within the range of Un+/- 10 % and all 10 mín mean r.m.s. values of the supply voltage shall be within the range of Un + 10%/- 15%. (acc. EN50160:2010, section 4.2.2) | [8 empty] | x |  | O
95 | 5F | reserved for future use
96 | 60 | reserved for future use
97 | 61 | reserved for future use
98 | 62 | reserved for future use
99 | 63 | reserved for future use
100 | 64 | Communication error M-Bus channel 1 | Indicates a communication problem when reading the meter connected to channel 1 of the M-Bus |  |  |  | x | [6 empty] | M-M
101 | 65 | Communication ok M-Bus channel 1 | Indicates that the communication with the M-Bus meter connected to channel 1 of the M-Bus is ok again. |  |  |  | x | [6 empty] | M-M
102 | 66 | Replace Battery M-Bus channel 1 | Indicates that the battery must be exchanged due to the expected end of life time. |  |  |  | x | [6 empty] | M-M
103 | 67 | Fraud attempt M-Bus channel 1 | Indicates that a fraud attempt has been registered. |  |  |  | x | [6 empty] | M-M
104 | 68 | Clock adjusted M-Bus channel 1 | Indicates that the clock has been adjusted. |  |  |  | x | [6 empty] | M-M
105 | 69 | New M-Bus device installed channel 1 | Indicated the meter (M-Bus master) has registered a M-Bus device connected to channel 1 with a new serial number |  |  |  | x | [6 empty] | M-M
106 | 6A | Permanent Error M-Bus channel 1 | Severe error reported by M-Bus device |  |  |  | x | [6 empty] | M-M
107 | 6B | reserved for future use
108 | 6C | reserved for future use
109 | 6D | reserved for future use
110 | 6E | Communication error M-bus channel 2 | Indicates a communication problem when reading the meter connected to channel 2 of the M-Bus |  |  |  | x | [6 empty] | M-M
111 | 6F | Communication ok M-bus channel 2 | Indicates that the communication with the M-Bus meter connected to channel 2 of the M-Bus is ok again. |  |  |  | x | [6 empty] | M-M
112 | 70 | Replace Battery M-Bus channel 2 | Indicates that the battery must be exchanged due to the expected end of life time. |  |  |  | x | [6 empty] | M-M
113 | 71 | Fraud attempt M-Bus channel 2 | Indicates that a fraud attempt has been registered in the M-Bus device. |  |  |  | x | [6 empty] | M-M
114 | 72 | Clock adjusted M-Bus channel 2 | Indicates that the clock has been adjusted. |  |  |  | x | [6 empty] | M-M
115 | 73 | New M-Bus device installed channel 2 | Indicated the meter (M-Bus master) has registered a M-Bus device connected to channel 2 with a new serial number |  |  |  | x | [6 empty] | M-M
116 | 74 | Permanent Error M-Bus channel 2 | Severe error reported by M-Bus device (Bit 3 in MBUS status EN13757) |  |  |  | x | [6 empty] | M-M
117 | 75 | reserved for future use
118 | 76 | reserved for future use
119 | 77 | reserved for future use
120 | 78 | Communication error M-bus channel 3 | Indicates a communication problem when reading the meter connected to channel 3 of the M-Bus |  |  |  | x | [6 empty] | M-M
121 | 79 | Communication ok M-bus channel 3 | Indicates that the communication with the M-Bus meter connected to channel 3 of the M-Bus is ok again. |  |  |  | x | [6 empty] | M-M
122 | 7A | Replace Battery M-Bus channel 3 | Indicates that the battery must be exchanged due to the expected end of life time. |  |  |  | x | [6 empty] | M-M
123 | 7B | Fraud attempt M-Bus channel 3 | Indicates that a fraud attempt has been registered. |  |  |  | x | [6 empty] | M-M
124 | 7C | Clock adjusted M-Bus channel 3 | Indicates that the clock has been adjusted. |  |  |  | x | [6 empty] | M-M
125 | 7D | New M-Bus device installed channel 3 | Indicated the meter (M-Bus master) has registered a M-Bus device connected to channel 3 with a new serial number |  |  |  | x | [6 empty] | M-M
126 | 7E | Permanent Error M-Bus channel 3 | Severe error reported by M-Bus device (Bit 3 in MBUS status EN13757) |  |  |  | x | [6 empty] | M-M
127 | 7F | reserved for future use
128 | 80 | reserved for future use
129 | 81 | reserved for future use
130 | 82 | Communication error M-bus channel 4 | Indicates a communication problem when reading the meter connected to channel 4 of the M-Bus |  |  |  | x | [6 empty] | M-M
131 | 83 | Communication ok M-bus channel 4 | Indicates that the communication with the M-Bus meter connected to channel 4 of the M-Bus is ok again. |  |  |  | x | [6 empty] | M-M
132 | 84 | Replace Battery M-Bus channel 4 | Indicates that the battery must be exchanged due to the expected end of life time. |  |  |  | x | [6 empty] | M-M
133 | 85 | Fraud attempt M-Bus channel 4 | Indicates that a fraud attempt has been registered. |  |  |  | x | [6 empty] | M-M
134 | 86 | Clock adjusted M-Bus channel 4 | Indicates that the clock has been adjusted. |  |  |  | x | [6 empty] | M-M
135 | 87 | New M-Bus device installed channel 4 | Indicated the meter (M-Bus master) has registered a M-Bus device connected to channel 4 with a new serial number |  |  |  | x | [6 empty] | M-M
136 | 88 | Permanent Error M-Bus channel 4 | Severe error reported by M-Bus device (Bit 3 in MBUS status EN13757) |  |  |  | x | [6 empty] | M-M
137 | 89 | reserved for future use
138 | 8A | reserved for future use
139 | 8B | reserved for future use
140 | 8C | No connection timeout | There has been no remote communication on application layer for a predefined period of time; i.e. meter could not be reached remotely. | [9 empty] | x | O
141 | 8D | Modem Initialization failure | Modem's response to initialization AT command(s) is invalid or ERROR or no response received | [9 empty] | x | M-G
142 | 8E | SIM Card failure | SIM card is not inserted or is not recognized. The detection of the SIM card status is supported by the corresponding AT commands as listed in 3GPP TS 27.007 | [9 empty] | x | M-G
143 | 8F | SIM Card ok | SIM card has been correctly detected | [9 empty] | x | M-G
144 | 90 | GSM registration failure | Modem's registration on GSM network was not successful | [9 empty] | x | M-G
145 | 91 | GPRS registration failure | Modem's registration on GPRS network was not successful | [9 empty] | x | M-G
146 | 92 | PDP context established | PDP context is established | [9 empty] | x | M-G
147 | 93 | PDP context destroyed | PDP context is destroyed | [9 empty] | x | M-G
148 | 94 | PDP context failure | No Valid PDP context(s) retrieved | [9 empty] | x | M-G
149 | 95 | Modem SW reset | Modem restarted by SW reset | [9 empty] | x | M-G
150 | 96 | Modem HW reset | Modem restarted by HW reset (this event is not issued after a general power resume) | [9 empty] | x | O
151 | 97 | GSM outgoing connection | Modem is successfully connected, initiated by an outgoing call. | [9 empty] | x | M-G
152 | 98 | GSM incoming connection | Modem is successfully connected, initiated by an incoming call | [9 empty] | x | M-G
153 | 99 | GSM hang-up | Modem is disconnected | [9 empty] | x | M-G
154 | 9A | Diagnostic failure | Modem's response to diagnostic AT command(s) ("+CPIN?", "+CSQ", "+CREG?", "+CGREG?", "+COPS?", "+CGACT?", "+CPMS?") is invalid or ERROR or no response received. | [9 empty] | x | O
155 | 9B | User initialization failure | Modem's initialization AT command(s ) – specified in attribute 3 of the modem configuration object - is invalid. Error message or no response from the modem. | [9 empty] | x | M-G
156 | 9C | Signal quality low | Signal strength too low, not known, or not detectable | [9 empty] | x | O
157 | 9D | Auto Answer Number of calls exceeded | Number of calls has exceeded (in mode(1) or mode(2) ) the values given in the attribute number_of_calls. | [9 empty] | x | M-G
158 | 9E | Local communication attempt | Indicates a successful communication on any local port has been initiated. | [9 empty] | x | O
159 | 9F | reserved for future use
160 | A0 | Manual disconnection M-Bus channel 1 | Indicates that the disconnector has been manually disconnected. |  |  |  |  | x | [5 empty] | O
161 | A1 | Manual connection M-Bus channel 1 | Indicates that the disconnector has been manually connected. |  |  |  |  | x | [5 empty] | O
162 | A2 | Remote disconnection M-Bus channel 1 | Indicates that the disconnector has been remotely disconnected. |  |  |  |  | x | [5 empty] | M-M
163 | A3 | Remote connection M-Bus channel 1 | Indicates that the disconnector has been remotely connected. |  |  |  |  | x | [5 empty] | M-M
164 | A4 | Valve alarm M-Bus channel 1 | Indicates that a valve alarm has been registered. |  |  |  |  | x | [5 empty] | O
165 | A5 | Local disconnection M-Bus channel 1 | Indicates that the disconnector has been locally disconnected. |  |  |  |  | x | [5 empty] | M-M
166 | A6 | Local connection M-Bus channel 1 | Indicates that the disconnector has been locally connected. |  |  |  |  | x | [5 empty] | M-M
167 | A7 | reserved for future use
168 | A8 | reserved for future use
169 | A9 | reserved for future use
170 | AA | Manual disconnection M-Bus channel 2 | Indicates that the disconnector has been manually disconnected. | [5 empty] | x |  |  |  |  | O
171 | AB | Manual connection M-Bus channel 2 | Indicates that the disconnector has been manually connected. | [5 empty] | x |  |  |  |  | O
172 | AC | Remote disconnection M-Bus channel 2 | Indicates that the disconnector has been remotely disconnected. | [5 empty] | x |  |  |  |  | M-M
173 | AD | Remote connection M-Bus channel 2 | Indicates that the disconnector has been remotely connected. | [5 empty] | x |  |  |  |  | M-M
174 | AE | Valve alarm M-Bus channel 2 | Indicates that a valve alarm has been registered. | [5 empty] | x |  |  |  |  | O
175 | AF | Local disconnection M-Bus channel 2 | Indicates that the disconnector has been locally disconnected. | [5 empty] | x |  |  |  |  | M-M
176 | B0 | Local connection M-Bus channel 2 | Indicates that the disconnector has been locally connected. | [5 empty] | x |  |  |  |  | M-M
177 | B1 | reserved for future use
178 | B2 | reserved for future use
179 | B3 | reserved for future use
180 | B4 | Manual disconnection M-Bus channel 3 | Indicates that the disconnector has been manually disconnected. | [6 empty] | x |  |  |  | O
181 | B5 | Manual connection M-Bus channel 3 | Indicates that the disconnector has been manually connected. | [6 empty] | x |  |  |  | O
182 | B6 | Remote disconnection M-Bus channel 3 | Indicates that the disconnector has been remotely disconnected. | [6 empty] | x |  |  |  | M-M
183 | B7 | Remote connection M-Bus channel 3 | Indicates that the disconnector has been remotely connected. | [6 empty] | x |  |  |  | M-M
184 | B8 | Valve alarm M-Bus channel 3 | Indicates that a valve alarm has been registered. | [6 empty] | x |  |  |  | O
185 | B9 | Local disconnection M-Bus channel 3 | Indicates that the disconnector has been locally disconnected. | [6 empty] | x |  |  |  | M-M
186 | BA | Local connection M-Bus channel 3 | Indicates that the disconnector has been locally connected. | [6 empty] | x |  |  |  | M-M
187 | BB | reserved for future use
188 | BC | reserved for future use
189 | BD | reserved for future use
190 | BE | Manual disconnection M-Bus channel 4 | Indicates that the disconnector has been manually disconnected. | [7 empty] | x |  |  | O
191 | BF | Manual connection M-Bus channel 4 | Indicates that the disconnector has been manually connected. | [7 empty] | x |  |  | O
192 | C0 | Remote disconnection M-Bus channel 4 | Indicates that the disconnector has been remotely disconnected. | [7 empty] | x |  |  | M-M
193 | C1 | Remote connection M-Bus channel 4 | Indicates that the disconnector has been remotely connected. | [7 empty] | x |  |  | M-M
194 | C2 | Valve alarm M-Bus channel 4 | Indicates that a valve alarm has been registered. | [7 empty] | x |  |  | O
195 | C3 | Local disconnection M-Bus channel 4 | Indicates that the disconnector has been locally disconnected. | [7 empty] | x |  |  | M-M
196 | C4 | Local connection M-Bus channel 4 | Indicates that the disconnector has been locally connected. | [7 empty] | x |  |  | M-M
197 | C5 | reserved for future use
198 | C6 | reserved for future use
199 | C7 | reserved for future use
200 | C8 | manufacturer specific
201 | C9 | manufacturer specific
202 | CA | manufacturer specific
203 | CB | manufacturer specific
204 | CC | manufacturer specific
205 | CD | manufacturer specific
206 | CE | manufacturer specific
207 | CF | manufacturer specific
208 | D0 | manufacturer specific
209 | D1 | manufacturer specific
210 | D2 | manufacturer specific
211 | D3 | manufacturer specific
212 | D4 | manufacturer specific
213 | D5 | manufacturer specific
214 | D6 | manufacturer specific
215 | D7 | manufacturer specific
216 | D8 | manufacturer specific
217 | D9 | manufacturer specific
218 | DA | manufacturer specific
219 | DB | manufacturer specific
220 | DC | manufacturer specific
221 | DD | manufacturer specific
222 | DE | manufacturer specific
223 | DF | manufacturer specific
224 | E0 | manufacturer specific
225 | E1 | manufacturer specific
226 | E2 | manufacturer specific
227 | E3 | manufacturer specific
228 | E4 | manufacturer specific
229 | E5 | manufacturer specific
230 | E6 | manufacturer specific
231 | E7 | manufacturer specific
232 | E8 | manufacturer specific
233 | E9 | manufacturer specific
234 | EA | manufacturer specific
235 | EB | manufacturer specific
236 | EC | manufacturer specific
237 | ED | manufacturer specific
238 | EE | manufacturer specific
239 | EF | manufacturer specific
240 | F0 | manufacturer specific
241 | F1 | manufacturer specific
242 | F2 | manufacturer specific
243 | F3 | manufacturer specific
244 | F4 | manufacturer specific
245 | F5 | manufacturer specific
246 | F6 | manufacturer specific
247 | F7 | manufacturer specific
248 | F8 | manufacturer specific
249 | F9 | manufacturer specific
250 | FA | manufacturer specific
251 | FB | manufacturer specific
252 | FC | manufacturer specific
253 | FD | manufacturer specific
254 | FE | Load profile cleared | Any of the profiles cleared. NOTE: If it appears in Standard Event Log then any of the E-load profiles was cleared. If the event appears in the M-Bus Event log then one of the M-Bus load profiles was cleared | x |  |  | x | [6 empty] | M
255 | FF | Event log cleared | Indicates that the event log was cleared. This is always the first entry in an event log. It is only stored in the affected event log. | x | x | x | x | x | x | x | x | x |  | M
EOF!

## Alarms
ALARM REGISTER 1 [0-0:97.98.0.255] |  |  | ALARM REGISTER 2 [0-0:97.98.1.255]
Bit | Alarm Name | Triggering Event | Bit | Alarm Name | Triggering Event
0 | Clock invalid | 6 | 0 | Total Power Failure | 1
1 | Battery replace | 7 | 1 | Power Resume | 2
2 | Reserved for future use | - | 2 | Voltage Phase Failure L1 | 82
3 | Reserved for future use | - | 3 | Voltage Phase Failure L2 | 83
4 | Reserved for future use | - | 4 | Voltage Phase Failure L3 | 84
5 | Reserved for future use | - | 5 | Voltage Phase Resume L1 | 85
6 | Reserved for future use | - | 6 | Voltage Phase Resume L2 | 86
7 | Reserved for future use | - | 7 | Voltage Phase Resume L3 | 87
8 | Program memory error | 12 | 8 | Missing Neutral | 89
9 | RAM error | 13 | 9 | Phase Asymmetry | 90
10 | NV memory error | 14 | 10 | Current Reversal | 91
11 | Measurement system error | 16 | 11 | Wrong Phase Sequence | 88
12 | Watchdog error | 15 | 12 | Unexpected Consumption | 52
13 | Fraud attempt | 40, 42, 44, 46, 49, 50[1] | 13 | Key Exchanged | 48
14 | Reserved for future use | - | 14 | Bad Voltage Quality L1 | 92
15 | Reserved for future use | - | 15 | Bad Voltage Quality L2 | 93
16 | M-Bus communication error ch1 | 100 | 16 | Bad Voltage Quality L3 | 94
17 | M-Bus communication error ch2 | 110 | 17 | External Alert | 20
18 | M-Bus communication error ch3 | 120 | 18 | Local communication attempt | 53
19 | M-Bus communication error ch4 | 130 | 19 | New M-Bus Device Installed Ch1 | 105
20 | M-Bus fraud attempt ch1 | 103 | 20 | New M-Bus Device Installed Ch2 | 115
21 | M-Bus fraud attempt ch2 | 113 | 21 | New M-Bus Device Installed Ch3 | 125
22 | M-Bus fraud attempt ch3 | 123 | 22 | New M-Bus Device Installed Ch4 | 135
23 | M-Bus fraud attempt ch4 | 133 | 23 | Reserved for future use | -
24 | Reserved for future use | - | 24 | Reserved for future use | -
25 | Reserved for future use | - | 25 | Reserved for future use | -
26 | Reserved for future use | - | 26 | Reserved for future use | -
27 | Reserved for future use | - | 27 | M-Bus valve alarm Ch1 | 164
28 | Reserved for future use | - | 28 | M-Bus valve alarm Ch2 | 174
29 | Reserved for future use | - | 29 | M-Bus valve alarm Ch3 | 184
30 | Reserved for future use | - | 30 | M-Bus valve alarm Ch4 | 194
31 | Reserved for future use | - | 31 | Disconnect/Reconnect Failure | 68
[1] Any of the listed events shall trigger the alarm.

## Extension D
Extension D
Objects concerning disconnector.
# | Object / Attribute Name | Supported Objects |  | IC |  | OBIS code
|  | 102 1ph IP | 103 3ph IP | Class | Ver. | OBIS code
| Disconnect control scheduler | M-D | M-D | 22 | 0 | 0-0:15.0.1.255
| Disconnector script table | M-D | M-D | 9 | 0 | 0-0:10.0.106.255
| Disconnect control | M-D | M-D | 70 | 0 | 0-0:96.3.10.255
| Event Object - Disconnector Control log | M-D | M-D | 1 | 0 | 0-0:96.11.2.255
| Disconnector Control Log | M-D | M-D | 7 | 1 | 0-0:99.98.2.255
| Limiter | M-D | M-D | 71 | 0 | 0-0:17.0.0.255
| Supervision monitor 1 - Fuse supervision L1 | M-D | M-D | 21 | 0 | 1-0:31.4.0.255
| Supervision monitor 2 - Fuse supervision L2 | NA | M-D | 21 | 0 | 1-0:51.4.0.255
| Supervision monitor 3 - Fuse supervision L3 | NA | M-D | 21 | 0 | 1-0:71.4.0.255
| Sliding Average current L1 (for fuse supervision) | M-D | M-D | 5 | 0 | 1-0:31.4.0.255
| Sliding Average current L2 (for fuse supervision) | NA | M-D | 5 | 0 | 1-0:51.4.0.255
| Sliding Average current L3 (for fuse supervision) | NA | M-D | 5 | 0 | 1-0:71.4.0.255
| Average Instantaneous Import Power (+A) | M-D | M-D | 5 | 0 | 1-0:1.24.0.255
| Average Instantaneous Net Power (¦+A¦-¦-A¦) | O | O | 5 | 0 | 1-0:16.24.0.255
| Average Instantaneous Total Power (¦+A¦+¦-A¦) | M-D | M-D | 5 | 0 | 1-0:15.24.0.255
M-D=mandatory for extension , O=optional, NA=not applicable

## Extension M
Extension M
Objects concerning Multi Utility
# | Object / Attribute Name | Supported Objects |  | IC |  | OBIS code
|  | 102 1ph IP | 103 3ph IP | Class | Ver. | OBIS code
| M-Bus master port setup 1 | M-M | M-M | 74 | 0 | 0-0:24.6.0.255
| M-Bus master port setup 2 | O | O | 74 | 0 | 0-1:24.6.0.255
| M-Bus client channel 1 | M-M | M-M | 72 | 0 | 0-1:24.1.0.255
| M-Bus client channel 2 | M-M | M-M | 72 | 0 | 0-2:24.1.0.255
| M-Bus client channel 3 | M-M | M-M | 72 | 0 | 0-3:24.1.0.255
| M-Bus client channel 4 | M-M | M-M | 72 | 0 | 0-4:24.1.0.255
| M-Bus Value channel 1, instance 1 | M-M | M-M | 4 | 0 | 0-1:24.2.1.255
| M-Bus Value channel 1, instance 2 | M-M | M-M | 4 | 0 | 0-1:24.2.2.255
| M-Bus Value channel 1, instance 3 | M-M | M-M | 4 | 0 | 0-1:24.2.3.255
| M-Bus Value channel 1, instance 4 | M-M | M-M | 4 | 0 | 0-1:24.2.4.255
| M-Bus Value channel 2, instance 1 | M-M | M-M | 4 | 0 | 0-2:24.2.1.255
| M-Bus Value channel 2, instance 2 | M-M | M-M | 4 | 0 | 0-2:24.2.2.255
| M-Bus Value channel 2, instance 3 | M-M | M-M | 4 | 0 | 0-2:24.2.3.255
| M-Bus Value channel 2, instance 4 | M-M | M-M | 4 | 0 | 0-2:24.2.4.255
| M-Bus Value channel 3, instance 1 | M-M | M-M | 4 | 0 | 0-3:24.2.1.255
| M-Bus Value channel 3, instance 2 | M-M | M-M | 4 | 0 | 0-3:24.2.2.255
| M-Bus Value channel 3, instance 3 | M-M | M-M | 4 | 0 | 0-3:24.2.3.255
| M-Bus Value channel 3, instance 4 | M-M | M-M | 4 | 0 | 0-3:24.2.4.255
| M-Bus Value channel 4, instance 1 | M-M | M-M | 4 | 0 | 0-4:24.2.1.255
| M-Bus Value channel 4, instance 2 | M-M | M-M | 4 | 0 | 0-4:24.2.2.255
| M-Bus Value channel 4, instance 3 | M-M | M-M | 4 | 0 | 0-4:24.2.3.255
| M-Bus Value channel 4, instance 4 | M-M | M-M | 4 | 0 | 0-4:24.2.4.255
| M-Bus Device ID 1 channel 1 | M-M | M-M | 1 | 0 | 0-1:96.1.0.255
| M-Bus Device ID 1 channel 2 | M-M | M-M | 1 | 0 | 0-2:96.1.0.255
| M-Bus Device ID 1 channel 3 | M-M | M-M | 1 | 0 | 0-3:96.1.0.255
| M-Bus Device ID 1 channel 4 | M-M | M-M | 1 | 0 | 0-4:96.1.0.255
| M-Bus Device ID 2 channel 1 | M-M | M-M | 1 | 0 | 0-1:96.1.1.255
| M-Bus Device ID 2 channel 2 | M-M | M-M | 1 | 0 | 0-2:96.1.1.255
| M-Bus Device ID 2 channel 3 | M-M | M-M | 1 | 0 | 0-3:96.1.1.255
| M-Bus Device ID 2 channel 4 | M-M | M-M | 1 | 0 | 0-4:96.1.1.255
| Profile status for M-Bus Master Load profile 1 | M-M | M-M | 1 | 0 | 0-1:96.10.3.255
| Profile status for M-Bus Master Load profile 2 | M-M | M-M | 1 | 0 | 0-2:96.10.3.255
| Profile status for M-Bus Master Load profile 3 | M-M | M-M | 1 | 0 | 0-3:96.10.3.255
| Profile status for M-Bus Master Load profile 4 | M-M | M-M | 1 | 0 | 0-4:96.10.3.255
| M-Bus Master Load profile for channel 1 | M-M | M-M | 7 | 1 | 0-1:24.3.0.255
| M-Bus Master Load profile for channel 2 | M-M | M-M | 7 | 1 | 0-2:24.3.0.255
| M-Bus Master Load profile for channel 3 | M-M | M-M | 7 | 1 | 0-3:24.3.0.255
| M-Bus Master Load profile for channel 4 | M-M | M-M | 7 | 1 | 0-4:24.3.0.255
| M-Bus Master Disconnect control object 1 | M-M | M-M | 70 | 0 | 0-1:24.4.0.255
| M-Bus Master Disconnect control object 2 | M-M | M-M | 70 | 0 | 0-2:24.4.0.255
| M-Bus Master Disconnect control object 3 | M-M | M-M | 70 | 0 | 0-3:24.4.0.255
| M-Bus Master Disconnect control object 4 | M-M | M-M | 70 | 0 | 0-4:24.4.0.255
| M-Bus Disconnect control scheduler | M-M | M-M | 22 | 0 | 0-1:15.0.1.255
| M-Bus Disconnector script table | M-M | M-M | 9 | 0 | 0-1:10.0.106.255
| Event Objects - M-Bus Master Control logs 1 | M-M | M-M | 1 | 0 | 0-1:96.11.4.255
| Event Objects - M-Bus Master Control logs 2 | M-M | M-M | 1 | 0 | 0-2:96.11.4.255
| Event Objects - M-Bus Master Control logs 3 | M-M | M-M | 1 | 0 | 0-3:96.11.4.255
| Event Objects - M-Bus Master Control logs 4 | M-M | M-M | 1 | 0 | 0-4:96.11.4.255
| M-Bus Master Control log object 1 | M-M | M-M | 7 | 1 | 0-1:24.5.0.255
| M-Bus Master Control log object 2 | M-M | M-M | 7 | 1 | 0-2:24.5.0.255
| M-Bus Master Control log object 3 | M-M | M-M | 7 | 1 | 0-3:24.5.0.255
| M-Bus Master Control log object 4 | M-M | M-M | 7 | 1 | 0-4:24.5.0.255
| Event Object - M-Bus Event Log | M-M | M-M | 1 | 1 | 0-0:96.11.3.255
| M-Bus Event Log | M-M | M-M | 7 | 1 | 0-0:99.98.3.255
M-M=mandatory for extension M, O=optional, NA=not applicable

## Extension L
Extension L
Objects concerning Load management with relays
# | Object / Attribute Name | Supported Objects |  | IC |  | OBIS code
|  | 102 1ph IP | 103 3ph IP | Class | Ver. | OBIS code
| Load Mgmt script table | M-L | M-L | 9 | 0 | 0-0:10.0.103.255
| Load Mgmt - Relay control 1 | M-L | M-L | 70 | 0 | 0-1:96.3.10.255
| Load Mgmt - Relay control 2 | O | O | 70 | 0 | 0-2:96.3.10.255
| Load Mgmt - Relay control N | O | O | 70 | 0 | 0-n:96.3.10.255
M-L=mandatory for extension L, O=optional, NA=not applicable

## Push objects (hidden)
PUSH Objects
Objects concerning Push
# | Object / Attribute Name | Supported Objects |  | IC |  | Default Value
|  | 102 | 103 | Class | Ver.
| Push setup - Interval_1 | M | M | 40 | 0 | 0-1:25.9.0.255
| Push setup - Interval_2 | M | M | 40 | 0 | 0-2:25.9.0.255
| Push setup - Interval_3 | M | M | 40 | 0 | 0-3:25.9.0.255
| Push setup - On Power down | M | M | 40 | 0 | 0-5:25.9.0.255
| Push action scheduler - Interval_1 | M | M | 22 | 0 | 0-1:15.0.4.255
| Push action scheduler - Interval_2 | M | M | 22 | 0 | 0-2:15.0.4.255
| Push action scheduler - Interval_3 | M | M | 22 | 0 | 0-3:15.0.4.255
# | Object / Attribute Name | Supported Objects |  | IC |  | Default Value
|  | 102 | 103 | Class | Ver.
| Push setup - Customer Information | O | O | 40 | 0 | 0-6:25.9.0.255
| Push action scheduler - Customer Information | O | O | 22 | 0 | 0-4:15.0.4.255
| Security setup - Customer Information | O | O | 64 | 0 | 0-0:43.0.1.255
| IEC HDLC setup - Consumer Information port | O | O | 23 | 1 | 0-1:22.0.0.255
M=mandatory, O=optional, NA=not applicable